## Notes
Notes:
Data filled in General and conclusion Sections will not upload in TIIMES. Please use these sections to keep data ready for copy paste.
Data in Item Description columns of Accepted Quantity and cumulative Accepted quantity must be verified thoroughly before uploading in TIIMES.
Pending activity, Areas of concern & Details of measuring instruments sheets are applicable for IVR.
Select options from drop down list for unit of measurement (Item Description) & certifying body of measuring instruments (Details of measuring instruments).
Do not modify this format.
To start next row in cell itself use below shortcut: press 'alt + Enter' keys together. Alt + Enter

## General
Note: - Data filled in this sheet will not upload in TIIMES
Title | Details
Control Number
SAP number
Notification Number
Project Name & Location
Client Name
End User Name
DEC / PMC / EPC Name
DEC / PMC / EPC Number
Vendor Name
PO Number (Client PO on Vendor)
Sub Vendor
PO Number (Vendor PO on Sub Vendor)
Inspection Location
Inspection Date(s)

## Item Description
Po Item No. | Item Code | Item Description | Unit | Po Quantity | Offered Quantity | Accepted Quantity (Please verify thouroghly before using this Column for IRN) | Cumulative Accepted Quanitity (for IRN Only)
100 | 4380145524 | CS, SEAMLESS, CONCENTRIC RED, BW,ANSI B16.9, ASTM A234 GR. WPB-S, SIZE 8" X 6" X SCH STD, GALV. | number | 3 | 3 | 3 | 3 | number
110 | 4380805602 | CS, SEAMLESS, CONCENTRIC RED, BW,ANSI B16.9, ASTM A234 GR. WPB-S, SIZE 8" X 6" X SCH STD, GALV. | number | 1 | 1 | 1 | 1 | meter
160 | 4388251844 | CS, SEAMLESS, TEE EQUAL, BW,ANSI B16.9, ASTM A234 GR. WPB-S, SIZE 8" X SCH STD, GALV. | number | 9 | 9 | 9 | 9 | km
210 | 4381595602 | CS, SEAMLESS, ECCENTRIC RED, BW,ANSI B16.9, ASTM A234 GR. WPB-S, SIZE 8" X 6" X SCH 40, GALV. | number | 4 | 4 | 4 | 4 | meter (number)
km (number)
each
Piece
Test sample
AU - All Unit
lot
Set
Running Meter
kg
metric ton (tonne)
ton
cubic millimetre
cubic centimeter
cubic meter
cubic inch
cubic foot
mm
cm
in
foot
mile
yard
liter
kl
cl
ml
g
lb
oz
Sq. mm
Sq. cm
Sq. meter
Sq. in
Sq. foot

## Reference Documents
Sr. No. | Document Name | Client Document Number | Vendor Document Number | Approval Status
1 | PR/MR/ARM | Not Applicable | Not Applicable | Not Applicable
2 | QAP/ITP/QCP | QAP No. 6746-IEX-00-EC-0001_B204 | Not Applicable | Provided by IOCL
3 | Drawing(s) | Not Applicable | Not Applicable | Not Applicable
4 | Procedure(s) | Not Applicable | Not Applicable | Not Applicable
5 | Datasheet(s) | Not Applicable | Not Applicable | Not Applicable
6 | Others (Specify) | Standard Specification for Colour Coding of Piping Material: 6-82-0003 Rev.3 | Not Applicable | Provided by IOCL

## Stages Witnessed
Stages Witnessed
ITP Sr. No.: C1 – Selection of sample for product testing – Found to meet applicable code and specification requirement.
ITP Sr. No.: C1.2– Product tensile and hardness test at NABL accredited lab on representative samples identified by TUV – Found to meet applicable code and specification requirement.
ITP Sr. No.: D1 – Visual inspection (100%) from offered lot of each line item – No injurious surface imperfections were observed.
ITP Sr. No.: D2 – Dimensional inspection randomly selected samples (10% - Min. 01 No.) from offered lot of each line item – Found to meet the code and standard requirement
ITP Sr. No.: D3 – DP test on bevel edges randomly selected samples (10% - Min. 01 No.) from offered lot of each line item – No surface indication were observed.
ITP Sr. No.: D4 – Product hardness of (10% - Min. 01 No.) by portable hardness tester ffrom offered lot of each line item. – Found within limit.
ITP Sr. No.: E– Marking verified of dimensionally inspected items from offered lot of each line item – Found in order.
ITP Sr. No.: D4 - Galvanizing coating verified 20% Qty. - Found to meet applicable code and specification requirements.
ITP Sr. No.: E– Stamping verified (100%) from offered line item – Found in order.
All measuring instruments/ equipment were verified for continued suitability for intended use, proper identification, calibration status, traceability to national standards & found satisfactory.

## Document reviewed
Document reviewed
ITP Sr. No.: A2 – Raw material test certificates reviewed for its technical content only as declared by manufacturer and endorsed by M/s. Topaz – Found to meet the material specification requirements.
ITP Sr. No.: B3 – HT chart /reports - Found in order
ITP Sr. No.: C1– Product chemical analysis lab test reports – Found to meet the applicable code and project specification requirement
ITP Sr. No.: D2 – Dimension reports – Found to meet the code and standard requirement.
ITP Sr. No.: D3 – DP test reports – Found in order.
ITP Sr. No.: E – Marking report - Found in order
ITP Sr. No.: J - Manufacturer test certificates no.: 8715/ 2023-24 R0 Dtd. 05.10.2023- Found to meet the material specification requirements.
Internal test/inspection reports, Calibration reports & pre-qualification type test report (earlier Qualified in witness of TPIA) of fittings - Found to meet the code specification requirement.

## Details of measuring instrument
Sr. No. | Detail of Equipment(s) / Instrument(s) | Range | ID | Validity till Date | Calibration Certificate Number | NABL / OTHER CERT. BODIES / NABL Traceability (type Yes wherever applicable) | NON-NABL (type Yes wherever applicable)
1 | Measuring Tape | 0-5 Mtr | MT/3Mtrs/01 | 05.02.2024 | MH/CL/23/02/126/NABL, Dtd:06.02.2023 | Yes |  | Yes
2 | Digital Ultrasonic Thickness Gauge | 2 to 200 mm | EDISON-1/ Sr. No. 6924-9140 | 21.12.2023 | MH/CL/22/12/626/NABL, Dtd:22.12.2022 | Yes |  | No
3 | Portable Hardness Tester | --- | PHT-01 | 15.12.2023 | MH/CL/22/12/161, Dtd:16.12.2022 | Yes

## Areas of concerns
Areas Of Concern
REMARKS:-- Photographs are not allowed by Vendor during inspection.

## Pending Activities
Pending Activities from this visit
None for this visit

## Conclusion
Note: Data filled in this sheet will not upload in TIIMES
Non Conformities raised / Discrepancies observed during Inspection (If Any, Mention TUV India NCR Number ):
None
Identification of Inspected Item(s):
Inspected 100% stamped (Witnessed double & rest Single ) as “ ” near manufacturers marking
Conclusion (Acceptable / Not Acceptable / Acceptance subject to):
Acceptable
IRN can be issued for PO Item numbers:
Expenses:
Remarks: