## Notes
Notes:
Data filled in General and conclusion Sections will not upload in TIIMES. Please use these sections to keep data ready for copy paste.
Data in Item Description columns of Accepted Quantity and cumulative Accepted quantity must be verified thoroughly before uploading in TIIMES.
Pending activity, Areas of concern & Details of measuring instruments sheets are applicable for IVR.
Select options from drop down list for unit of measurement (Item Description) & certifying body of measuring instruments (Details of measuring instruments).
Do not modify this format.
To start next row in cell itself use below shortcut: press 'alt + Enter' keys together. Alt + Enter

## General
Note: - Data filled in this sheet will not upload in TIIMES
Title | Details
Control Number
SAP number
Notification Number
Project Name & Location
Client Name
End User Name
DEC / PMC / EPC Name
DEC / PMC / EPC Number
Vendor Name
PO Number (Client PO on Vendor)
Sub Vendor
PO Number (Vendor PO on Sub Vendor)
Inspection Location
Inspection Date(s)

## Item Description
Po Item No. | Item Code | Item Description | Unit | Po Quantity | Offered Quantity | Accepted Quantity (Please verify thouroghly before using this Column for IRN) | Cumulative Accepted Quanitity (for IRN Only)
1 | 90020913 | CS+PTFE On Off Ball Valve Size: 40NB (Valve Sr. No-210807517 To 210807518) | number | 2 | 2 | 2 | 2 | number
2 | 90020914 | CS+PTFE On Off Ball Valve Size: 50NB (Valve Sr. No-210807519 To 210807550) | number | 32 | 32 | 32 | 32 | meter
3 | 90020915 | CS+PTFE On Off Ball Valve Size: 80NB Valve Sr. No-(210807551) | number | 1 | 1 | 1 | 1 | km
4 | 90020916 | CS+PTFE On Off Ball Valve Size: 100NB ( Valve Sr. No-210807552 To 210807555) | number | 4 | 4 | 4 | 4 | meter (number)
5 | 90012991 | CS On-Off Valve Specification : Type: Ball, Size: 25mm (Valve Sr. No-210807245 To 210807250) | number | 6 | 6 | 6 | 6 | km (number)
6 | 90012992 | CS On-Off Valve Specification : Type: Ball, Size: 40mm (Valve Sr. No-210807251 To 210807288) | number | 38 | 38 | 38 | 38 | each
7 | 90012993 | CS On-Off Valve Specification : Type: Ball, Size: 50mm (210807289 To 210807326) | number | 38 | 38 | 38 | 38 | Piece
8 | 90012994 | CS On-Off Valve Specification : Type: Ball, Size: 80mm (Valve Sr. No-210807327 To 210807345) | number | 19 | 19 | 19 | 19 | Test sample
9 | 90013010 | SS304 On-Off Valve Specification : Type: Ball, Size: 25mm (210807199 To 210807216) | number | 18 | 18 | 18 | 18 | AU - All Unit
10 | 90013011 | SS304 On-Off Valve Specification : Type: Ball, Size: 40mm (Valve Sr. No-210807217 To 210807220) | number | 4 | 4 | 4 | 4 | lot
11 | 90013012 | SS304 On-Off Valve Specification : Type: Ball, Size: 50mm (Valve Sr. No-210807221 To 210807228) | number | 8 | 8 | 8 | 8 | Set
12 | 90013013 | SS304 On-Off Valve Specification : Type: Ball, Size: 80mm (Valve Sr. No- 210807229 To 210807244) | number | 16 | 16 | 16 | 16 | Running Meter
13 | 90013001 | SS316 On-Off Valve Specification : Type: Ball, Size: 50mm (Valve Sr. No-210807347 To 210807423 & 210807900 To 210807975) | number | 153 | 153 | 153 | 153 | kg
14 | 90013002 | SS316 On-Off Valve Specification : Type: Ball, Size: 80mm (Valve Sr. No-210807499 To 210807512) | number | 14 | 14 | 14 | 14 | metric ton (tonne)
15 | 90013003 | SS316 On-Off Valve Specification : Type: Ball, Size: 100mm (210807513 To 210807516) | number | 4 | 4 | 4 | 4 | ton
16 | 90013020 | CS On-Off Valve Specification : Type: BS Globe, Size:50mm (Valve Sr. No-210807573 To 210807580) | number | 8 | 8 | 8 | 8 | cubic millimetre
17 | 90012992 | CS On-Off Valve Specification : Type: Ball, Size: 40mm (Valve Sr. No-210807556 To 210807568) | number | 13 | 13 | 13 | 13 | cubic centimeter
18 | 90012993 | CS On-Off Valve Specification : Type: Ball, Size: 50mm (Valve Sr. No-210807569 To 210807570) | number | 2 | 2 | 2 | 2 | cubic meter
19 | 90012994 | CS On-Off Valve Specification : Type: Ball, Size: 80mm (Valve Sr. No-210807571 To 210807572) | number | 2 | 2 | 2 | 2 | cubic inch
cubic foot
mm
cm
in
foot
mile
yard
liter
kl
cl
ml
g
lb
oz
Sq. mm
Sq. cm
Sq. meter
Sq. in
Sq. foot

## Reference Documents
Sr. No. | Document Name | Client Document Number | Vendor Document Number | Approval Status
1 | PR/MR/ARM | NA
2 | QAP/ITP/QCP | NA | SO2122/00930 Rev No : 00 | Approved By Catasynth
3 | Drawing(s) |  | MP-GA-6749 ( 21 Sheets ) | Approved By Catasynth email 07/09/2021
4 | Procedure(s) | NA
5 | Datasheet(s) | NA | SO2122/00930-02 | Approved By Catasynth Email
6 | Others (Specify)

## Stages Witnessed
Stages Witnessed
As per QAP Stage 3.1 : Hydro Shell , hydro seat , Pneumatic seat tested 10 % of the offered selected Qty test pressure as per data sheet & approved GAD & test duration as per EN 12266 no leakage found .
As per QAP Stage 3.3 : Dimension , visual , clean ness ,Completed ness witnessed 10 % of offered selected Qty visual Tag no, serial no , size , rating , Model , operating pressure on Nmae plate as per data sheet , approved GAD found satsfactory , Dimension witness as per Approved GAD found satisfactory ,measued deviation dimension high lighted on GAD .

## Document reviewed
Document reviewed
As per QAP stage 1.1 : MTC for Body , adpt , Ball reviewed as per Data sheet , GAD & relevant stanadard found satisfactry .
As per QAP stage 3.0 : Pressure test report , visual , dimension reviewed as per GAD , DATA Sheet , relevant stanadrd found satisfacoty , Compliance report for 100 % pressure test testing , manufctured Part of ball valves 100 % compliance report verified & Noted.

## Details of measuring instrument
Sr. No. | Detail of Equipment(s) / Instrument(s) | Range | ID | Validity till Date | Calibration Certificate Number | NABL / OTHER CERT. BODIES / NABL Traceability (type Yes wherever applicable) | NON-NABL (type Yes wherever applicable)
1 | pressure gauge | 42 kg /sqcm | PG11 | 2021-12-05 | LH/M-ET/121-053 | Yes |  | Yes
2 | pressure gauge | 70 kg /sqcm | PG-12 | 2021-11-13 | LH/M-ET/H21-111 | YES |  | No
3 | pressure gauge | 70 kg /sqcm | 125875 | 2021-11-13 | LH/M-ET/H21-110 | YES
4 | pressure gauge | 21KG/SQCM | T9001 | 2021-12-07 | 44447-T9001 | YES
8 | pressure gauge | 14KG/SQCM | PG-10 | 2021-12-05 | 44445-PG-10 | YES
6 | Vernier Caliper | 300mm | 17553440 | 2022-10-20 | 44490-17553440 | YES
7 | Vernier Caliper | 600MM | 417556 | 2022-02-16 | 44244-417556 | YES
8 | pressure gauge | 210KG/SQCM | D23233 | 2021-12-05 | LH/M-ET/121-051 | YES

## Areas of concerns
Areas Of Concern
Devistion dimension high lighted on Approved GAD vendor to be in incorporate the Dimension & make as build send to client for approval .
As per PO mention DATA sheet no QT2122/00282-4 but inspection done as per vendor provided DATA sheet no- SO2122/00930-2 client acceptance required for the same.

## Pending Activities
Pending Activities from this visit

## Conclusion
Note: Data filled in this sheet will not upload in TIIMES
Non Conformities raised / Discrepancies observed during Inspection (If Any, Mention TUV India NCR Number ):
Identification of Inspected Item(s):
Conclusion (Acceptable / Not Acceptable / Acceptance subject to):
IRN can be issued for PO Item numbers:
Expenses:
Remarks: