## Notes
Notes:
Data filled in General and conclusion Sections will not upload in TIIMES. Please use these sections to keep data ready for copy paste.
Data in Item Description columns of Accepted Quantity and cumulative Accepted quantity must be verified thoroughly before uploading in TIIMES.
Pending activity, Areas of concern & Details of measuring instruments sheets are applicable for IVR.
Select options from drop down list for unit of measurement (Item Description) & certifying body of measuring instruments (Details of measuring instruments).
Do not modify this format.
To start next row in cell itself use below shortcut: press 'alt + Enter' keys together. Alt + Enter

## General
Note: - Data filled in this sheet will not upload in TIIMES
Title | Details
Control Number
SAP number
Notification Number
Project Name & Location
Client Name
End User Name
DEC / PMC / EPC Name
DEC / PMC / EPC Number
Vendor Name
PO Number (Client PO on Vendor)
Sub Vendor
PO Number (Vendor PO on Sub Vendor)
Inspection Location
Inspection Date(s)

## Item Description
Po Item No. | Item Code | Item Description | Unit | Po Quantity | Offered Quantity | Accepted Quantity (Please verify thouroghly before using this Column for IRN) | Cumulative Accepted Quanitity (for IRN Only)
1 | P022000000053 | REACTOR STATIONERY, SIZE- ID 2350 MM, TL TO TL 6600 MM, THK TOP- 16+8, THK BOTTOM- 22+8, CAPACITY- 32 KL, MOC- FRP, TAG NO. R-43114 A/B/C | number | 3 | 1 (Tag no. R-43114-A) | 1 | 1 | number
meter
km
meter (number)
km (number)
each
Piece
Test sample
AU - All Unit
lot
Set
Running Meter
kg
metric ton (tonne)
ton
cubic millimetre
cubic centimeter
cubic meter
cubic inch
cubic foot
mm
cm
in
foot
mile
yard
liter
kl
cl
ml
g
lb
oz
Sq. mm
Sq. cm
Sq. meter
Sq. in
Sq. foot

## Reference Documents
Sr. No. | Document Name | Client Document Number | Vendor Document Number | Approval Status
1 | PR/MR/ARM
2 | QAP/ITP/QCP |  | QP/FRP/CT 54/Rev. 01, Date- 29.04.2022 | Approved by M/s PCPL
3 | Drawing(s) |  | 1) CPE 41812, Rev. 3, 2) CPE 10837, Rev. 1. | Approved by M/s PCPL
4 | Procedure(s)
5 | Datasheet(s)
6 | Others (Specify)

## Stages Witnessed
Stages Witnessed
QAP Sr. No. 3 a, b, c & d (Cut-out/Coupon testing) - Witnessed Tensile test, Lap shear strength test, Glass content test & Barcol hardness test on machined specimen from shell cut-out which was drawn & prepared by vendor - Found to meet the QAP & Drawing requirements.
QAP Sr. No. 4 a (Workmanship) - Visual inspection carried out from inside & outside on accessible surface only after completion of all manufacturing activities - Found to meet the requirements.
QAP Sr. No. 4 b & c (Final Dimension) - Nozzle orientation checked & dimension inspection carried out as per approved drawing - Found to meet the drawing requirements.

## Document reviewed
Document reviewed
QAP Sr. No. 1 A & B (Raw Materials) - Raw material test certificates for Resin, Surface mat, Chopped strand mat, Uni directional mat, Rovings, PPH sheet & PPH Pipe were reviewed for its contents only, as declared by manufacturer and endorsed by vendor - Found to meet the requirements.
QAP Sr. No. 2 A & B (Progress inspection) Manufacturer's internal in process inspection reports reviewed for Mould inspection & Dimensions - Found to meet the drawing requirements.
Calibration certificates reviewed for measuring & testing instruments used - Found to meet the requirements.

## Details of measuring instrument
Sr. No. | Detail of Equipment(s) / Instrument(s) | Range | ID | Validity till Date | Calibration Certificate Number | NABL / OTHER CERT. BODIES / NABL Traceability (type Yes wherever applicable) | NON-NABL (type Yes wherever applicable)
1 | Measuring Tape | 0-5 Mtr | MT-05M-01 | 23.03.2023 | KES/220324/D/005, Dtate- 25.03.2022 | Yes |  | Yes
2 | Measuring Tape | 0-15 Mtr | MT-15M-01 | 23.03.2023 | KES/220324/D/003, Date- 25.03.2022 | Yes |  | No
3 | Digital Vernier Caliper | 0-300 mm | 20044 | 29.04.2023 | KES/220430/D/008, Date- 30.04.2022 | Yes
4 | Barcol Hardness Tester | 0-100 Barcol | 056104 | 08.04.2023 | VEA/05/2022-23, Date- 09.04.2023 |  | Yes
5 | Universal Testing Machine | 0-200 KN | MUTM/01 | 07.01.2023 | MATRIX/CAL/2021-22/01/2243, Date- 08.01.2022 | Yes
6 | Temperature Controller | 0-1200 Deg. C | 141100739 | 22.09.2022 | KES/21230903437, Date- 24.09.2021 |  | Yes
7 | Weighing Scale | 0-300 Grams | U-2900004 | 22.03.2023 | 2278189/VAD/2022/01, Date- 22.03.2022 |  | No

## Areas of concerns
Areas Of Concern
None for this visit.

## Pending Activities
Pending Activities from this visit
As per approved QAP for applicable Tag numbers.

## Conclusion
Note: Data filled in this sheet will not upload in TIIMES
Non Conformities raised / Discrepancies observed during Inspection (If Any, Mention TUV India NCR Number ):
None
Identification of Inspected Item(s):
Selected samples identified with single hard stamp as " " on the face for mechanical testing.
Conclusion (Acceptable / Not Acceptable / Acceptance subject to):
Acceptable subjected to result of mechanical testing.
IRN can be issued for PO Item numbers:
Expenses:
Remarks: