## Notes
Notes:
Data filled in General and conclusion Sections will not upload in TIIMES. Please use these sections to keep data ready for copy paste.
Data in Item Description columns of Accepted Quantity and cumulative Accepted quantity must be verified thoroughly before uploading in TIIMES.
Pending activity, Areas of concern & Details of measuring instruments sheets are applicable for IVR.
Select options from drop down list for unit of measurement (Item Description) & certifying body of measuring instruments (Details of measuring instruments).
Do not modify this format.
To start next row in cell itself use below shortcut: press 'alt + Enter' keys together. Alt + Enter

## General
Note: - Data filled in this sheet will not upload in TIIMES
Title | Details
Control Number
SAP number
Notification Number
Project Name & Location
Client Name
End User Name
DEC / PMC / EPC Name
DEC / PMC / EPC Number
Vendor Name
PO Number (Client PO on Vendor)
Sub Vendor
PO Number (Vendor PO on Sub Vendor)
Inspection Location
Inspection Date(s)

## Item Description
Po Item No. | Item Code | Item Description | Unit | Po Quantity | Offered Quantity | Accepted Quantity (Please verify thouroghly before using this Column for IRN) | Cumulative Accepted Quanitity (for IRN Only)
00010 | 0708112822 | Ball Valve , 63 Plain End , Without Stem IGL Kanpur | number | 15 | 15 | 15 | 15 | number
00020 | 0708112823 | Ball Valve , 125 Plain End , Without Stem IGL New Delhi | number | 10 | 10 | 10 | 10 | meter
00030 | 0708112823 | Ball Valve , 125 Plain End , Without Stem IGL Ghaziabad | number | 10 | 10 | 10 | 10 | km
00040 | 0708112823 | Ball Valve , 125 Plain End , Without Stem IGL Muzaffar Nagar | number | 10 | 10 | 10 | 10 | meter (number)
00050 | 0708112823 | Ball Valve , 125 Plain End , Without Stem IGL Kanpur | number | 10 | 10 | 10 | 10 | km (number)
each
Piece
Test sample
AU - All Unit
lot
Set
Running Meter
kg
metric ton (tonne)
ton
cubic millimetre
cubic centimeter
cubic meter
cubic inch
cubic foot
mm
cm
in
foot
mile
yard
liter
kl
cl
ml
g
lb
oz
Sq. mm
Sq. cm
Sq. meter
Sq. in
Sq. foot

## Reference Documents
Sr. No. | Document Name | Client Document Number | Vendor Document Number | Approval Status
1 | PR/MR/ARM | Not Applicable | Not Applicable | Not Applicable
2 | QAP/ITP/QCP | Not Applicable | For EF Fittings : QAP-IGL-01 Rev - 01 Date : 16.07.2021 For Ball Valves : QAP-IGL-03 Rev - 01 Date : 18.08.2021 | For EF Fittings & Ball Valves: Approved by Consultant Tractebel Engineering Pvt. Ltd in code “A”.
3 | Drawing(s) | Not Applicable | For EF Fittings : 700.600.693. R-00 ; 700.600.892. R-00 ; For Ball Valve : 141 127 C1 Com 05Y30 125 Com | For EF Fittings Manufacturing Drawings , For Ball Valve , drawings are approved by consultant Tractebal Engineering Pvt. Ltd. In code "D".
4 | Procedure(s) | Not Applicable | Not Applicable | Not Applicable
5 | Datasheet(s) | Not Applicable | Not Applicable | Not Applicable
6 | Others (Specify) | Not Applicable | Not Applicable | Not Applicable

## Stages Witnessed
Stages Witnessed
For EF Fittings - 125 & 63 MM Coupler for Ball Valve as per QAP No - QAP - IGL - 01 Rev - 01
As per QAP Clause No: 4 - Crush De-cohesion test witnessed for 63 mm OD Coupler – Found Satisfactory.
As per QAP Clause No: 5 - Peel De-cohesion test witnessed for 125 mm OD Coupler – Found Satisfactory.
As per QAP Clause No: 9 - Electric resistance test of randomly selected fittings of each size & type witnessed – Found Satisfactory.
As per QAP Clause No: 10 - Thermal Stability test for Oxidation induction time witnessed for 30 minutes at 200 Deg. C - found satisfactory.
As per QAP Clause No: 11 – Melt Mass Flow rate (MFR) test at 190 Deg. C temperature & 5 kg weight witnessed – Found Satisfactory.
As per QAP Clause No: 12 - Dimensional inspection for randomly selected 05 Nos. of fitting of each size & type checked - found as per manufacturer drawing and found within tolerance. b. Visual check – Found free of injurious defects.
As per QAP Clause No : 13 - Storage for final products monitored – found satisfactory.
As per QAP Clause No: 14 – Product identification marking verified for 05 nos. of fitting of each size & type - found in order.
As per QAP Clause No : 15 – Inspection reports as per QAP requirement verified – found in order.
For - 125 & 63 MM Ball Valve as per QAP No - QAP - IGL - 03 Rev - 01
As per QAP Clause No: 2 - Dimensional inspection for randomly selected 05 Nos. of valve of each size & type / lot checked - found as per manufacturer drawing and found within tolerance. b. Visual check – Found free of injurious defects.
As per QAP Clause No: 11 – Product identification marking verified for 05 nos. of fitting of each size & type / lot - found in order.
As per QAP Clause No : 12 - Storage for final products monitored – found satisfactory.
As per QAP Clause No : 13 – Inspection reports as per QAP requirement verified – found in order.

## Document reviewed
Document reviewed
For EF Fittings - 125 & 63 MM Coupler for Ball Valve as per QAP No - QAP - IGL - 01 Rev - 01
As per QAP Clause No : 1 - Raw material test certificate as declared by vendor reviewed – Found in order.
As per QAP Clause No : 2 - Internal inspection report for Hydrostatic strength at 80 Deg C. reviewed - found in order.
As per QAP Clause No : 3 - Type test certificate for hydrostatic test at 20 Deg C. as declared by vendor reviewed - found in order.
For - 125 & 63 MM Ball Valve as per QAP No - QAP - IGL - 03 Rev - 01
As per QAP Clause No : 1 - Raw material test certificate as declared by vendor reviewed – Found in order.
As per QAP Clause No : 3 - Manufacturer Test Certificate for Hydrostatic strength at 80 Deg C. reviewed - found in order.
As per QAP Clause No : 4 & 5 - Mfg. Test Certificate for Leak tightness of seat & packing at different temeprature , test pressure & holding time as mentioned in the approved QAP reveiwed - found in order.
As per QAP Clause No : 6 - Type test certificate for Impact strength test reviewed - found in order.
As per QAP Clause No : 7 - Manufacturer test certificate for valve operating torque as provided by vendor reviewed - found in order.
As per QAP Clause No : 8, 9 & 10 - Type test certificate for Pressure drop , oxidation induction time (thermal stability) & Melt Mass flow rate (MFR) as provided by vendor reviewed - found in order.
Calibration test certificate of Instrument used for inspection reviewed, Found in order.

## Details of measuring instrument
Sr. No. | Detail of Equipment(s) / Instrument(s) | Range | ID | Validity till Date | Calibration Certificate Number | NABL / OTHER CERT. BODIES / NABL Traceability (type Yes wherever applicable) | NON-NABL (type Yes wherever applicable)
1 | Dial Caliper | 0 - 300 mm | QA-DV-06 | 25.12.2022 | SE/21/12/1296 Dt : 26.12.2021 | Yes |  | Yes
2 | Timer | 0-10 Min. | QA-TM-01 | 27.09.2022 | E2021/09/307 Dt: 27.09.2021 | Yes |  | No
3 | Digital Temperature Controller | 0-230 Deg C | QA-TC-04 | 27.09.2022 | E2021/09/305 Dt : 27.09.2021 | Yes
4 | Weighing Balance | 0 - 600 gm | QA-WS-01 | 27.09.2022 | M2021/09/412 Dt: 27.09.2021 | Yes
5 | Dummy Weight | 5 Kg | QA-W-02 | 27.09.2022 | M2021/09/414 Dt: 27.09.2021 | Yes
6 | Micro Ohm Meter | 20 m ohm - 2000 Ohm | QA-MC-05 | 27.05.2022 | E2021/05/158 Dt:27.05.2021 | Yes
7 | Measuring Scale | 0 - 100 cm | QA-Rule-01 | 15.12.2022 | M2017/12/038 Dt : 15.12.2017 |  | Yes

## Areas of concerns
Areas Of Concern
None

## Pending Activities
Pending Activities from this visit
None

## Conclusion
Note: Data filled in this sheet will not upload in TIIMES
Non Conformities raised / Discrepancies observed during Inspection (If Any, Mention TUV India NCR Number ):
Identification of Inspected Item(s):
Conclusion (Acceptable / Not Acceptable / Acceptance subject to):
IRN can be issued for PO Item numbers:
Expenses:
Remarks: