## Notes
Notes:
Data filled in General and conclusion Sections will not upload in TIIMES. Please use these sections to keep data ready for copy paste.
Data in Item Description columns of Accepted Quantity and cumulative Accepted quantity must be verified thoroughly before uploading in TIIMES.
Pending activity, Areas of concern & Details of measuring instruments sheets are applicable for IVR.
Select options from drop down list for unit of measurement (Item Description) & certifying body of measuring instruments (Details of measuring instruments).
Do not modify this format.
To start next row in cell itself use below shortcut: press 'alt + Enter' keys together. Alt + Enter

## General
Note: - Data filled in this sheet will not upload in TIIMES
Title | Details
Control Number
SAP number
Notification Number
Project Name & Location
Client Name
End User Name
DEC / PMC / EPC Name
DEC / PMC / EPC Number
Vendor Name
PO Number (Client PO on Vendor)
Sub Vendor
PO Number (Vendor PO on Sub Vendor)
Inspection Location
Inspection Date(s)

## Item Description
Po Item No. | Item Code | Item Description | Unit | Po Quantity | Offered Quantity | Accepted Quantity (Please verify thouroghly before using this Column for IRN) | Cumulative Accepted Quanitity (for IRN Only)
8 | MR5597 | VESSEL:SS304, MIXER,10 KL,2800(H)X2200(ID) PU PALLETTE MIXER Tag No- MIX-A521 & MIX-A522 | number | 5 | 2 | 2 | 2
number
meter
km
meter (number)
km (number)
each
Piece
Test sample
AU - All Unit
lot
Set
Running Meter
kg
metric ton (tonne)
ton
cubic millimetre
cubic centimeter
cubic meter
cubic inch
cubic foot
mm
cm
in
foot
mile
yard
liter
kl
cl
ml
g
lb
oz
Sq. mm
Sq. cm
Sq. meter
Sq. in
Sq. foot

## Reference Documents
Sr. No. | Document Name | Client Document Number | Vendor Document Number | Approval Status
1 | PR/MR/ARM
2 | QAP/ITP/QCP |  | APS/QAP2602, Rev-1 | Approved by TUV.
3 | Drawing(s) |  | APS26021601 Rev-02 | Approved by TCE in code-2.
4 | Procedure(s)
5 | Datasheet(s)
6 | Others (Specify)

## Stages Witnessed
Stages Witnessed
As per QAP stage no 3 - Raw material identification witnessed for Shell, dish, bottom cone, nozzle pipe & nozzle flanges- found acceptable.
As per QAP stage no 4C - Dished Head & bottom cone dimensional inspection & DP test witnessed- found acceptable.
As per QAP stage no 4.D - Long seam & Cir. Seam random witnessed- found acceptable.
As per QAP stage no 5.A - Final dimensional inspection witnessed- found acceptable.
As per QAP stage no 5.B - Water fill up test witnessed- found acceptable.

## Document reviewed
Document reviewed
As per QAP stage no 3.D - Non pressure parts material history chart & test certificates reviewed- found in order.
As per QAP stage no 4 A - Welding procedure & welder qualification report reviewed- found in order.
As per QAP stage no 4.B - NDT, shop procedures reviewed.
As per QAP stage no 4.E - L-seam & C-seam back chip DP test report reviewed- found in order.
As per QAP stage no 4.F - Butt weld RT summary, weld map & report reviewed- found in order.
As per QAP stage no 4.G - Nozzle to shell & dish fit up report reviewed- found in order.
As per QAP stage no 4.H - Nozzle weld back chip DP test report reviewed- found in order.
As per QAP stage no 4.I - Pneumatic test report reviewed, found in order.
As per QAP stage no 5.A - Surface finish report reviewed, found in order.

## Details of measuring instrument
Sr. No. | Detail of Equipment(s) / Instrument(s) | Range | ID | Validity till Date | Calibration Certificate Number | NABL / OTHER CERT. BODIES / NABL Traceability (type Yes wherever applicable) | NON-NABL (type Yes wherever applicable)
Yes
No

## Areas of concerns
Areas Of Concern
Drawings are not approved by client.
As per previous IVR no- IVR050103176922/1-58 Rev. 0 Dated: 03/01/2022 area of concern points are still open.

## Pending Activities
Pending Activities from this visit

## Conclusion
Note: Data filled in this sheet will not upload in TIIMES
Non Conformities raised / Discrepancies observed during Inspection (If Any, Mention TUV India NCR Number ):
Identification of Inspected Item(s):
Tag number hard punched on liffing lugs for every vessel.
Conclusion (Acceptable / Not Acceptable / Acceptance subject to):
IRN can be issued for PO Item numbers:
Expenses:
Remarks: