## Notes
Notes:
Data filled in General and conclusion Sections will not upload in TIIMES. Please use these sections to keep data ready for copy paste.
Data in Item Description columns of Accepted Quantity and cumulative Accepted quantity must be verified thoroughly before uploading in TIIMES.
Pending activity, Areas of concern & Details of measuring instruments sheets are applicable for IVR.
Select options from drop down list for unit of measurement (Item Description) & certifying body of measuring instruments (Details of measuring instruments).
Do not modify this format.
To start next row in cell itself use below shortcut: press 'alt + Enter' keys together. Alt + Enter

## General
Note: - Data filled in this sheet will not upload in TIIMES
Title | Details
Control Number
SAP number
Notification Number
Project Name & Location
Client Name
End User Name
DEC / PMC / EPC Name
DEC / PMC / EPC Number
Vendor Name
PO Number (Client PO on Vendor)
Sub Vendor
PO Number (Vendor PO on Sub Vendor)
Inspection Location
Inspection Date(s)

## Item Description
Po Item No. | Item Code | Item Description | Unit | Po Quantity | Offered Quantity | Accepted Quantity (Please verify thouroghly before using this Column for IRN) | Cumulative Accepted Quanitity (for IRN Only)
1 | 4013488 | 30KL VERTICAL CONICAL STORAGE TANK, MOC: SS-316L, SIZE: 2850 MM DIA X 4750 MM HEIGHT | each | 1 | 1 | 1 | 1
number
meter
km
meter (number)
km (number)
each
Piece
Test sample
AU - All Unit
lot
Set
Running Meter
kg
metric ton (tonne)
ton
cubic millimetre
cubic centimeter
cubic meter
cubic inch
cubic foot
mm
cm
in
foot
mile
yard
liter
kl
cl
ml
g
lb
oz
Sq. mm
Sq. cm
Sq. meter
Sq. in
Sq. foot

## Reference Documents
Sr. No. | Document Name | Client Document Number | Vendor Document Number | Approval Status
1 | PR/MR/ARM | Not Applicable | Not Applicable | Not Applicable
2 | QAP/ITP/QCP | Not Applicable | ATAW-QAP-22-23-012 REV.0 | Approved by Client on Dt. 08.12.2022
3 | Drawing(s) | Not Applicable | ATAW/GA/22-23/012 REV.1 Sheel 1 of 2 & 2 of 2 | Approved by Client on Dt. 08.12.2022
4 | Procedure(s) | Not Applicable | Not Applicable | Not Applicable
5 | Datasheet(s) | Not Applicable | Not Applicable | Not Applicable
6 | Others (Specify) | Not Applicable | Not Applicable | Not Applicable

## Stages Witnessed
Stages Witnessed
QAP Sr. No.1, Raw material identification of pressure parts i.e Plates and of Pipes­­ Found to meet the material specification requirements
QAP Sr. No.11 & 13: (Final Dimension Check & Visual Inspection): ­ Final dimension of complete tank checked after completion of all manufacturing activities ­ Found to meet the drawing requirement.
QAP Sr. No.12 & 13: (Inspection of Complete Weld & Visual Inspection): ­ Visual inspection carried out from outside surface on accessible area only ­ No major surface defects were observed.
QAP Sr. No.14: (Hydro static Test): Witnessed of Hydro test at full of water for Holding Period of 1hr. ­ Visual Inspection carried out on all weld joints and surface of the Job ­ No leakage observed during holding period.
QAP Sr. No.15: Name plate verifiedand Stamping, Nozzle No. N1, N5, N8, N9 and Manhole (MH1 & MH2) (Fitment of Blind flange, Gasket and Stud & nut) verified as per the drawing - found in order.
All measuring instruments/ equipment were verified for continued suitability for intended use, proper identification, calibration status, traceability to national standards & found satisfactory.

## Document reviewed
Document reviewed
QAP Sr. No. 1 ­ Raw material test certificates (Pressure part of Pipes and Plates) reviewed for its technical content only as declared by manufacturer and endorsed by ATAW – Found to meet the applicable code requirement.
QAP Sr. No. 2 & 3: (Raw Material ­ Non Pressure Part): ­ Raw material test certificates as declared by manufacturer and endorse and provided by vendor were reviewed for non­pressure part (Flanges, Fittings, Fastners, Gasket, Plate & C­channel etc. - Non pressure part itmes) ­ Found to meet the requirement.
QAP Sr. No. 5: (WPS/PQR/WPQ): ­ WPS/PQR/WPQ records reviewed (Already reviewed by M/s. TUV) ­ Found to meet the requirement.
QAP Sr. No. 6: (Welding Consumables): ­ Weld consumable test certificates as declared by manufacturer and endorse and provided by vendor were reviewed ­ Found to meet the requirement.
QAP Sr. No. 7: (Set­ups: Shell L/S, C/S & Nozzle Joints): ­ Set­up reports reviewed for Shell L/S, C/S & Nozzle Joints ­ Found to meet the requirement.
QAP Sr. No. 8: (100% LPT after B/C and Welding of L/S & C/S): ­ Lequid penetrant test reports reviewed for Back­chip, Final L/S & C/S weld joint ­ Found to meet the requirement.
QAP Sr. No. 10: (Pneumatic Test of R F Pads): ­ R F Pad pneumatic test reports reviewed ­ Found to meet the client requirement as per mail.
QAP Sr. No. 16: Final dossier document verified as per Drawing and QAP - found in order.

## Details of measuring instrument
Sr. No. | Detail of Equipment(s) / Instrument(s) | Range | ID | Validity till Date | Calibration Certificate Number | NABL / OTHER CERT. BODIES / NABL Traceability (type Yes wherever applicable) | NON-NABL (type Yes wherever applicable)
Yes
No

## Areas of concerns
Areas Of Concern

## Pending Activities
Pending Activities from this visit

## Conclusion
Note: Data filled in this sheet will not upload in TIIMES
Non Conformities raised / Discrepancies observed during Inspection (If Any, Mention TUV India NCR Number ):
- None.
Identification of Inspected Item(s):
Conclusion (Acceptable / Not Acceptable / Acceptance subject to):
- Acceptable.
IRN can be issued for PO Item numbers:
Expenses:
Remarks: