## Notes
Notes:
Data filled in General and conclusion Sections will not upload in TIIMES. Please use these sections to keep data ready for copy paste.
Data in Item Description columns of Accepted Quantity and cumulative Accepted quantity must be verified thoroughly before uploading in TIIMES.
Pending activity, Areas of concern & Details of measuring instruments sheets are applicable for IVR.
Select options from drop down list for unit of measurement (Item Description) & certifying body of measuring instruments (Details of measuring instruments).
Do not modify this format.
To start next row in cell itself use below shortcut: press 'alt + Enter' keys together. Alt + Enter

## General
Note: - Data filled in this sheet will not upload in TIIMES
Title | Details
Control Number
SAP number
Notification Number
Project Name & Location
Client Name
End User Name
DEC / PMC / EPC Name
DEC / PMC / EPC Number
Vendor Name
PO Number (Client PO on Vendor)
Sub Vendor
PO Number (Vendor PO on Sub Vendor)
Inspection Location
Inspection Date(s)

## Item Description
Po Item No. | Item Code | Item Description | Unit | Po Quantity | Offered Quantity | Accepted Quantity (Please verify thouroghly before using this Column for IRN) | Cumulative Accepted Quanitity (for IRN Only)
10 | CH000087599 | CS SMLS PIPE 100NB SCHSTD BW IBR,ASTM 106 GR B HEAT NO : 3120305 MAKE : JSL | meter (number) | 66 Meter | 68.64 (11 NOS) | 68.64 (11 NOS) | 68.64 (11 NOS) | number
20 | CH000087568 | CS SMLS PIPE 15NB SCHXS PE,,ASTM 106 GR B HEAT NO : M003951B MAKE : JSL | meter (number) | 12 Meter | 12 ( 2 NOS ) | 12 ( 2 NOS ) | 12 ( 2 NOS ) | meter
30 | CH000087573 | CS SMLS PIPE 20NB SCHXS PE A106 GR B HEAT NO : M002669B MAKE : JSL | meter (number) | 6 Meter | 6.14 ( 1 NO ) | 6.14 ( 1 NO ) | 6.14 ( 1 NO ) | km
40 | CH000024507 | CS SMLS PIPE 20NB SCHXS PE IBR,A106 GR B HEAT NO : M002669B MAKE : JSL | meter (number) | 6 Meter | 6.39 ( 1 NO ) | 6.39 ( 1 NO ) | 6.39 ( 1 NO ) | meter (number)
50 | CH000087576 | CS SMLS PIPE 25NB SCHXS PE A106 GR B HEAT NO : M002965B MAKE : JSL | meter (number) | 384 Meter | 387.61 ( 62 NOS) | 387.61 ( 62 NOS) | 387.61 ( 62 NOS) | km (number)
60 | CH000024518 | CS SMLS PIPE 25NB SCHXS PE IBR,A106 GR B HEAT NO : M002965B MAKE : JSL | meter (number) | 48 Meter | 50.22 ( 8 NOS ) | 50.22 ( 8 NOS ) | 50.22 ( 8 NOS ) | each
70 | CH000087579 | CS SMLS PIPE 40NB SCHXS PE A106 GR B HEAT NO : 3873N MAKE : ISMT | meter (number) | 738 Meter | 742.55 ( 121 NOS) | 742.55 ( 121 NOS) | 742.55 ( 121 NOS) | Piece
80 | CH000024656 | CS SMLS PIPE 40NB SCHXS PE ,IBR, A106 GR B HEAT NO : 3873N MAKE : ISMT | meter (number) | 66 Meter | 68.2 ( 11 NOS) | 68.2 ( 11 NOS) | 68.2 ( 11 NOS) | Test sample
90 | CH000024817 | CS SMLS PIPE 50NB SCHXS BE IBR, A106 GR B HEAT NO : 3686N MAKE : ISMT | meter (number) | 30 Meter | 30.35 ( 5 NOS ) | 30.35 ( 5 NOS ) | 30.35 ( 5 NOS ) | AU - All Unit
100 | CH000087584 | CS SMLS PIPE 50NB SCHXS BE , A106 GR B HEAT NO : 3686N MAKE : ISMT | meter (number) | 222 Meter | 224.69 ( 37 NOS ) | 224.69 ( 37 NOS ) | 224.69 ( 37 NOS ) | lot
110 | CH000087587 | CS SMLS PIPE 80NB SCHSTD BW,A 106 GR B HEAT NO : M003939B MAKE : JSL | meter (number) | 174 Meter | 172.75 ( 29 NOS ) | 172.75 ( 29 Nos ) | 172.75 ( 29 NOS ) | Set
120 | CH000024144 | MS ERW PIPE 100NB CL-C , SCHEDULE-HEAVY ,BE ,IS-1239 PART-1 MAKE : JINDAL | meter (number) | 144 Meter | 144.72 ( 24 NOS ) | 144.72 ( 24 NOS ) | 144.72 ( 24 NOS ) | Running Meter
130 | CH000024153 | MS ERW PIPE 150NB CL-C BE, SCHEDULE -HEAVY ,IS-1239 PART-1 MAKE : JINDAL | meter (number) | 408 Meter | 410.04 ( 68 NOS) | 410.04 ( 68 NOS) | 410.04 ( 68 NOS) | kg
140 | CH000037289 | MS ERW PIPE 200NB THK-6.3mm BE ,IS 3589 GR 330 MAKE : JINDAL | meter (number) | 6 Meter | 6.05 ( 1 NOS ) | 6.05 ( 1 NOS ) | 6.05 ( 1 NOS ) | metric ton (tonne)
150 | CH000087595 | MS ERW PIPE 250NB THK-8mm BE ,IS 3589 FE 410 MAKE : TATA | meter (number) | 102 Meter | 102.25 ( 17 NOS ) | 102.25 ( 17 NOS ) | 102.25 ( 17 NOS ) | ton
160 | CH000024654 | MS ERW PIPE 350NB THK-8mm BE,,IS 3589 FE 410 MAKE : TATA | meter (number) | 6 Meter | 6.01 (1 NO ) | 6.01 (1 NO ) | 6.01 (1 NO ) | cubic millimetre
170 | CH000024555 | MS ERW PIPE 450NB THK-8mm,IS 3589 FE 410 MAKE : TATA | meter (number) | 6 Meter | 5.98 ( 1 NO ) | 5.98 ( 1 NO ) | 5.98 ( 1 NO ) | cubic centimeter
180 | CH000034657 | MS ERW PIPE 50NB SCH HVY BE,IS-1239 PART-1 MAKE : JINDAL | meter (number) | 444 Meter | 446.22 ( 74 NOS) | 446.22 ( 74 NOS) | 446.22 ( 74 NOS) | cubic meter
190 | CH000024001 | MS ERW PIPE 50NB SCH HVY BE,IS-1239 PART-1 MAKE : JINDAL | meter (number) | 168 Meter | 168.84 ( 28 NOS) | 168.84 ( 28 NOS) | 168.84 ( 28 NOS) | cubic inch
cubic foot
mm
cm
in
foot
mile
yard
liter
kl
cl
ml
g
lb
oz
Sq. mm
Sq. cm
Sq. meter
Sq. in
Sq. foot

## Reference Documents
Sr. No. | Document Name | Client Document Number | Vendor Document Number | Approval Status
1 | PR/MR/ARM
2 | QAP/ITP/QCP |  | TTI/20-21/QAP/AARTI/2197 Dtd : 05.01.2020 | Approved with comments by client
3 | Drawing(s)
4 | Procedure(s)
5 | Datasheet(s)
6 | Others (Specify)

## Stages Witnessed
Stages Witnessed
As per QAP Clause : 2 , Visual inspection carried out for 10 % qty. from each offered PO line item on accessible locations - No injurious surface defects were observed at the time of inspection
As per QAP Clause : 3, Dimension check carried out for 10 % qty. from each offered PO line item- Found to meet the standard / Specification requriements.
As per QAP Clause : 4, Marking correlated with Original TC for 10 % qty. from each offered PO line item- Found in order.

## Document reviewed
Document reviewed
As per QAP Clause :1,4 & 8 - Reviewed original TC of all offered pipes - Found to meet the material specification requirements , Photocopy of TC Endorsed .
Verified calibration validity & traceability of measuring instruments.

## Details of measuring instrument
Sr. No. | Detail of Equipment(s) / Instrument(s) | Range | ID | Validity till Date | Calibration Certificate Number | NABL / OTHER CERT. BODIES / NABL Traceability (type Yes wherever applicable) | NON-NABL (type Yes wherever applicable)
1 | Vernier caliper |  |  | 30.10.2022 |  | Yes |  | Yes
2 | measuring tape |  |  | 01.02.2022 |  |  |  | No

## Areas of concerns
Areas Of Concern
FOR PO Sr.No : 15,16 & 17 , Grade mentioned in PO is IS 3589 E 330 where as vendor has offered grades of IS 3589 E 410

## Pending Activities
Pending Activities from this visit
None

## Conclusion
Note: Data filled in this sheet will not upload in TIIMES
Non Conformities raised / Discrepancies observed during Inspection (If Any, Mention TUV India NCR Number ):
Identification of Inspected Item(s):
Conclusion (Acceptable / Not Acceptable / Acceptance subject to):
IRN can be issued for PO Item numbers:
Expenses:
Remarks: