## Notes
Notes:
Data filled in General and conclusion Sections will not upload in TIIMES. Please use these sections to keep data ready for copy paste.
Data in Item Description columns of Accepted Quantity and cumulative Accepted quantity must be verified thoroughly before uploading in TIIMES.
Pending activity, Areas of concern & Details of measuring instruments sheets are applicable for IVR.
Select options from drop down list for unit of measurement (Item Description) & certifying body of measuring instruments (Details of measuring instruments).
Do not modify this format.
To start next row in cell itself use below shortcut: press 'alt + Enter' keys together. Alt + Enter

## General
Note: - Data filled in this sheet will not upload in TIIMES
Title | Details
Control Number
SAP number
Notification Number
Project Name & Location
Client Name
End User Name
DEC / PMC / EPC Name
DEC / PMC / EPC Number
Vendor Name
PO Number (Client PO on Vendor)
Sub Vendor
PO Number (Vendor PO on Sub Vendor)
Inspection Location
Inspection Date(s)

## Item Description
Po Item No. | Item Code | Item Description | Unit | Po Quantity | Offered Quantity | Accepted Quantity (Please verify thouroghly before using this Column for IRN) | Cumulative Accepted Quanitity (for IRN Only)
00050 | 0814000110 | Saddle Tapp. MDPE 63 X 20 mm PE80/ PE100 | number | 500 | 500 | 500 | 500 | number
00060 | 0814000210 | Saddle Tapp. MDPE 63 X 32 mm PE80/ PE100 | number | 50 | 50 | 50 | 50 | meter
00070 | 0815000210 | Reducer MDPE 63 X 32 PE80/ PE100 WTH CPLR | number | 300 | 300 | 300 | 300 | km
00080 | 0818012810 | End Cap MDPE 32 mm EF PE80/ PE100 | number | 150 | 150 | 150 | 150 | meter (number)
00090 | 1011000010 | TR. Fitting PE To SS 20mm X 1/2" PE80/100 | number | 9679 | 9679 | 9679 | 9679 | km (number)
each
Piece
Test sample
AU - All Unit
lot
Set
Running Meter
kg
metric ton (tonne)
ton
cubic millimetre
cubic centimeter
cubic meter
cubic inch
cubic foot
mm
cm
in
foot
mile
yard
liter
kl
cl
ml
g
lb
oz
Sq. mm
Sq. cm
Sq. meter
Sq. in
Sq. foot

## Reference Documents
Sr. No. | Document Name | Client Document Number | Vendor Document Number | Approval Status
1 | PR/MR/ARM | Not Applicable | Not Applicable | Not Applicable
2 | QAP/ITP/QCP | Not Applicable | QAP-IGL-01 Rev: 01 | Approved by Tractebel On Dated. 20.07.2021
3 | Drawing(s) | Not Applicable | 1) 800.100.014 Rev:00 2) 700.600.892 Rev:00 3) 700.600.891 Rev:00 4) 800.600.896 Rev:00 5) 700.600.890 Rev:00 6) 700.600.888 Rev:00 | Approved by KPSL
4 | Procedure(s) | Not Applicable | Not Applicable | Not Applicable
5 | Datasheet(s) | Not Applicable | Not Applicable | Not Applicable
6 | Others (Specify) | Not Applicable | Not Applicable | Not Applicable

## Stages Witnessed
Stages Witnessed
As per QAP Clause No. 4, Crush Decohesion test witnessed in sampling basis as per BS EN 1555-7 - Found in order.
As per QAP Clause No. 9, Electric Resistance test witnessed in sampling basis as per BS EN 1555-7- Found in order.
As per QAP Clause No. 10, Oxidation induction time (Thermal Stability) test witnessed in sampling basis as per BS EN 1555-7 - Found in order.
As per QAP Clause No.11, Melt Mass Flow Rate (MFR) test witnessed in sampling basis as per BS EN 1555-7 - Found in order.
As per QAP Clause No. 12 Dimensional Inspection witnessed for 05 nos./size/ type from lot size as per manufacturer drawing - Found in order.
As per QAP Clause No. 13 Storage visually monitored - Found satisfactory.
As per QAP Clause No. 14 Marking randomly checked for 05 nos./size/ type from lot size - Found satisfactory.

## Document reviewed
Document reviewed
As per QAP Clause No. 1, Raw Material TC reviewed - Found in order.
As per QAP Clause No. 2 Hydrostatics strength at 80 Deg. Cent. report reviewed - Found in order.
As per QAP Clause No. 3 Hydrostatics strength at 20 Deg. Cent. report reviewed - Found in order.
As per QAP Clause No. 6 Tensile strength for butt fusion report reviewed - Found in order.
As per QAP Clause No. 7, Impact strength test report reviewed - Found in order.
As per QAP Clause No. 8, Pressure drop report reviewed - Found in order.

## Details of measuring instrument
Sr. No. | Detail of Equipment(s) / Instrument(s) | Range | ID | Validity till Date | Calibration Certificate Number | NABL / OTHER CERT. BODIES / NABL Traceability (type Yes wherever applicable) | NON-NABL (type Yes wherever applicable)
1 | Dial Caliper | 0 to 300 mm | QA-DV-06 | 18.12.2021 | M2020/12/1091 Dated.18.12.2020 | Yes |  | Yes
2 | Digital Temperature Controller | 0 To 230 Deg Celsius | QA-TC-04 | 27.09.2022 | E2021/09/305 Dated. 27.09.2021 | Yes |  | No
3 | Timer | 0 To 10 Min | QA-TM-01 | 27.09.2022 | E2021/09/307 Dated. 27.09.2021 | Yes
4 | Dial Caliper (Inner Calliper) | 0 To 200 mm | QA-DV-04 | 28.09.2022 | M2021/09/1018 Dated. 28.09.2021 | Yes
5 | Micro Ohm meter | 20 micro Ohm to 2000 Ohm | QA-MC-05 | 27.05.2022 | E2021/05/158 Dated.27.05.2021 | Yes
6 | Weighing Balance | 0 To 600 g | QA-WS-01 | 27.09.2022 | M2021/09/412 Dated.27.09.2021 | Yes

## Areas of concerns
Areas Of Concern
Nil

## Pending Activities
Pending Activities from this visit
Nil

## Conclusion
Note: Data filled in this sheet will not upload in TIIMES
Non Conformities raised / Discrepancies observed during Inspection (If Any, Mention TUV India NCR Number ):
Identification of Inspected Item(s):
Conclusion (Acceptable / Not Acceptable / Acceptance subject to):
IRN can be issued for PO Item numbers:
Expenses:
Remarks: