## Notes
Notes:
Data filled in General and conclusion Sections will not upload in TIIMES. Please use these sections to keep data ready for copy paste.
Data in Item Description columns of Accepted Quantity and cumulative Accepted quantity must be verified thoroughly before uploading in TIIMES.
Pending activity, Areas of concern & Details of measuring instruments sheets are applicable for IVR.
Select options from drop down list for unit of measurement (Item Description) & certifying body of measuring instruments (Details of measuring instruments).
Do not modify this format.
To start next row in cell itself use below shortcut: press 'alt + Enter' keys together. Alt + Enter

## General
Note: - Data filled in this sheet will not upload in TIIMES
Title | Details
Control Number
SAP number
Notification Number
Project Name & Location
Client Name
End User Name
DEC / PMC / EPC Name
DEC / PMC / EPC Number
Vendor Name
PO Number (Client PO on Vendor)
Sub Vendor
PO Number (Vendor PO on Sub Vendor)
Inspection Location
Inspection Date(s)

## Item Description
Po Item No. | Item Code | Item Description | Unit | Po Quantity | Offered Quantity | Accepted Quantity (Please verify thouroghly before using this Column for IRN) | Cumulative Accepted Quanitity (for IRN Only)
27 | GLAM3ZZA3B | SS316 DOUBLE COMPRESSION CABLE GLANDS-EX d II B, 16 MM CABLE GLAND AND ACCESSORIES, CABLE GLAND - DOUBLE COMPRESSION WITH PVC HOOD ( FOR WIRE ARMOURED CABLE ), M20X1.5P(M), EXD, IIC, MATERIAL SS316 IDent Code : I2349703165 | number | 502 | 502 | 502 |  | number
24 | GLAF2ZZA3B | SS316 DOUBLE COMPRESSION CABLE GLANDS-EX d II C CABLE GLAND AND ACCESSORIES, CABLE GLAND - DOUBLE COMPRESSION WITH PVC HOOD ( FOR WIRE ARMOURED CABLE ), 3/4" NPT(M), EXD, IIC, MATERIAL SS316 IDent Code : I2349703162 | number | 942 | 551 | 551 |  | meter
31 | GLJYYBCZ3B | SS316 ADAPTOR / REDUCER, 1" NPT (M) X 3/4" NPT (F) CABLE GLAND AND ACCESSORIES, ADAPTOR / REDUCER, 1" NPT (M) X 3/4" NPT (F), EXD, IIC, MATERIAL SS316 IDent Code : I2349703169 | number | 5 | 5 | 5 |  | km
19 | GLJYYBVZ3B | SS316 ADAPTOR / REDUCER, 1/2" NPT (M) X 3/4" NPT (F) CABLE GLAND AND ACCESSORIES, ADAPTOR / REDUCER, 3/4" NPT (F) X 1/2" NPT (M), EXD, IIC, MATERIAL SS316 IDent Code : I2349703171 | number | 565 | 565 | 565 |  | meter (number)
18 | GLAF4ZZA3B | SS316 DOUBLE COMPRESSION CABLE GLANDS-EX d II C CABLE GLAND AND ACCESSORIES, CABLE GLAND - DOUBLE COMPRESSION WITH PVC HOOD ( FOR WIRE ARMOURED CABLE ), 1 1/4" NPT(M), EXD, IIC, MATERIAL SS316 IDent Code : I2349703156 | number | 404 | 12 | 12 |  | km (number)
32 | GLJYYXXZ3B | SS316 ADAPTOR / REDUCER, 1" NPT (M) X 1 1/4" NPT (F) CABLE GLAND AND ACCESSORIES, ADAPTOR / REDUCER, 1" NPT(M) X 1 1/4" NPT(F), EXD, IIC, MATERIAL SS316 IDent Code : I2349703170 | number | 35 | 35 | 35 |  | each
29 | GLJYYBGZ3B | SS316 ADAPTOR / REDUCER, 1 1/2" NPT (M) x 1 1/4" NPT (F) CABLE GLAND AND ACCESSORIES, ADAPTOR / REDUCER, 1 1/2" NPT (M) X 1 1/4" NPT (F), EXD, IIC, MATERIAL SS316 IDent Code : I2349703167 | number | 75 | 75 | 75 |  | Piece
30 | GLJYYBEZ3B | SS316 ADAPTOR / REDUCER, 1 1/4" NPT (M) x 1" NPT (F) CABLE GLAND AND ACCESSORIES, ADAPTOR / REDUCER, 1 1/4" NPT (M) X 1" NPT (F), EXD, IIC, MATERIAL SS316 IDent Code : I2349703168 | number | 1 | 1 | 1 |  | Test sample
12 | JAF1DGP42E | JUNCTION BOX WITH BOTTOM ENTRY, 12P x 1.5mm2, EX e JUNCTION BOX WITH BOTTOM ENTRY, 12 NOS. OF 1/2" BRANCH CABLE ENTRIES, 1 1/4" MAIN CABLE ENTRY, SCREWLESS TYPE, 48 NOS. OF TERMINALS, EX 'E' IIC, IP IDent Code : I2103343830 | number | 95 | 95 | 95 |  | AU - All Unit
16 | ENCSPARES | SS PLUG FWPG-551- 1/2" NPT- 77Nos FWPG-553- 1" NPT- 21Nos FWPG-554- 1 1/4" NPT-10Nos IDent Code : I2103343832 | Lot | 1 | 1 | 1 |  | lot
21 | GLAF1ZZA3B | SS316 DOUBLE COMPRESSION CABLE GLANDS-EX d II B,20 MM CABLE GLAND AND ACCESSORIES, CABLE GLAND - DOUBLE COMPRESSION WITH PVC HOOD ( FOR WIRE ARMOURED CABLE ), 1/2" NPT(M), EXD, IIC, MATERIAL SS316 IDent Code : I2349703159 | number | 3216 | 502 | 502 |  | Set
Running Meter
kg
metric ton (tonne)
ton
cubic millimetre
cubic centimeter
cubic meter
cubic inch
cubic foot
mm
cm
in
foot
mile
yard
liter
kl
cl
ml
g
lb
oz
Sq. mm
Sq. cm
Sq. meter
Sq. in
Sq. foot

## Reference Documents
Sr. No. | Document Name | Client Document Number | Vendor Document Number | Approval Status
1 | PR/MR/ARM | HBDH-PD-INC-MRP-AXKP401-0001, Rev.02 |  | Code-R Approved by M/s EIL
2 | QAP/ITP/QCP |  | 2956A_2201106, 2956B_2201106, 2956C_2201106 & 2956D_2201106, Rev.01 | Code-A Approved by M/s TOYO and M/s TUV IPL
3 | Drawing(s) | HBDH-VD-000-INC-ARG-AXKP401-003, Rev.08 | 2201106, Rev.08 | Code-A Approved by M/s TOYO
4 | Procedure(s)
5 | Datasheet(s)
6 | Others (Specify)

## Stages Witnessed
Stages Witnessed
As per IS2500/2000 Part-1 samples are selected for final inspection. Selected sample Junction Boxes Tag Nos. are 109-JBA-1501, 109-JBN-1030, 109-JBN-1040,109-JBS-1612, 115-JBA-1513, 115-JBN-1405, 115-JBN-1417 & 115-JBA-1108 .
Below activities carried out on the selected sample Exe Junction Boxes: As per QAP Clause IV-1, 9 & 10: Visual inspection of enclosure for finish, Clear printing of Serial No, Certification Marking, Finish of Gaskets, Din Rails, Terminals, Earthing & BOM Check carried out on the Offered Junction Boxes as per approved drawings-Found Satisfactory. As per QAP Clause IV-2: Witnessed continuity check between terminals and earthing/body- Found satisfactory. As per QAP Clause IV-3&5: Witnessed insulation resistance test (before & after H.V test)- Found the insulation resistance values are more than 100 Mega Ohms (Test Voltage 1000V DC). As per QAP Clause IV-4: Witnessed HV test (test voltage 1.5 kV AC for 1minute)- Found withstood the same. As per QAP Clause IV-7: Mounting/Overall dimensional check carried out for length, width, height of the enclosures, thickness of the enclosure and gland plate- Found the values are within the tolerances as specified in the approved drawing. As per QAP Clause IV-8: No of cable entries verified- Found meeting the drawing requirements.
Below activities carried out on the selected sample Exd Cable Glands, Blanking Plugs & Accessories: As per QAP Clause III-1: Visual check for the offered glands finish (free from burrs, damages and sharp corner)- Found no burrs, no damages and no sharp corners. As per QAP Clause III-2: Overall Dimensional check carried out on the selected sample Cable Glands, Blanking Plugs & Accessories- Found Satisfactory. As per QAP Clause III-3: Assembly & Fitment internal and external verified on the selected sample Cable Glands, Blanking Plugs & Accessories- Found Satisfactory. As per QAP Clause III-4: Engraving details (Certification Markings) are verified on the selected sample Cable Glands, Blanking Plugs & Accessories- Found Satisfactory.

## Document reviewed
Document reviewed
As per QAP Clause I: Reviewed Raw Materials Test Certificates of LM6 (Enclosure), Electrical Components, Gaskets, Fasteners, Cable glands, Stopping plugs & Accessories of the offered Items- Found in order and attested for records.
As per QAP Clause II & IV-7: Reviewed Manufacturer Quality Assurance Certificate of the offered JBs- Found in order and attested for records.
As per QAP Clause III: Reviewed Type approval Certificates (CIMFR, PESO & BIS) for the offered JBs, Cable Glands, Stopping Plugs & Accessories- Found in order and reports attested for records.
Verified Calibration Status of the instruments used for inspection- Found valid calibration and attested for records.

## Details of measuring instrument
Sr. No. | Detail of Equipment(s) / Instrument(s) | Range | ID | Validity till Date | Calibration Certificate Number | NABL / OTHER CERT. BODIES / NABL Traceability (type Yes wherever applicable) | NON-NABL (type Yes wherever applicable)
1 | AC High Voltage Tester | 0-3kV | S1907022 | 2022-03-03 | MSIR/410321/39003 | Yes |  | Yes
2 | Digital Insulation Tester | ___ | 1907003642 | 2022-09-03 | MSIR/410921/28001 | Yes |  | No
3 | Vernier Caliper | 0-300mm | 12330001 | 2022-08-12 | 04-120821-003 | Yes

## Areas of concerns
Areas Of Concern

## Pending Activities
Pending Activities from this visit

## Conclusion
Note: Data filled in this sheet will not upload in TIIMES
Non Conformities raised / Discrepancies observed during Inspection (If Any, Mention TUV India NCR Number ):
Identification of Inspected Item(s):
Conclusion (Acceptable / Not Acceptable / Acceptance subject to):
IRN can be issued for PO Item numbers:
Expenses:
Remarks: