## Notes
Notes:
Data filled in General and conclusion Sections will not upload in TIIMES. Please use these sections to keep data ready for copy paste.
Data in Item Description columns of Accepted Quantity and cumulative Accepted quantity must be verified thoroughly before uploading in TIIMES.
Pending activity, Areas of concern & Details of measuring instruments sheets are applicable for IVR.
Select options from drop down list for unit of measurement (Item Description) & certifying body of measuring instruments (Details of measuring instruments).
Do not modify this format.
To start next row in cell itself use below shortcut: press 'alt + Enter' keys together. Alt + Enter

## General
Note: - Data filled in this sheet will not upload in TIIMES
Title | Details
Control Number
SAP number
Notification Number
Project Name & Location
Client Name
End User Name
DEC / PMC / EPC Name
DEC / PMC / EPC Number
Vendor Name
PO Number (Client PO on Vendor)
Sub Vendor
PO Number (Vendor PO on Sub Vendor)
Inspection Location
Inspection Date(s)

## Item Description
Po Item No. | Item Code | Item Description | Unit | Po Quantity | Offered Quantity | Accepted Quantity (Please verify thouroghly before using this Column for IRN) | Cumulative Accepted Quanitity (for IRN Only)
1 | 2001613521 | BLIND SPECTACLE, FF, 2" x 150#, ASTM A240 Grade 304L, Standard Drawing ASME B16.48, 125-250 AARH | number | 5 | 5 | 5 | 5 | number
meter
km
meter (number)
km (number)
each
Piece
Test sample
AU - All Unit
lot
Set
Running Meter
kg
metric ton (tonne)
ton
cubic millimetre
cubic centimeter
cubic meter
cubic inch
cubic foot
mm
cm
in
foot
mile
yard
liter
kl
cl
ml
g
lb
oz
Sq. mm
Sq. cm
Sq. meter
Sq. in
Sq. foot

## Reference Documents
Sr. No. | Document Name | Client Document Number | Vendor Document Number | Approval Status
1 | PR/MR/ARM | 10080-1-SS-PP-004 (Part -III) Rev.03, Dt. 22.01.2014 | Not Applicable | Issued by M/s RIL
2 | QAP/ITP/QCP | Annexure-6 _ ITP for SS Forged & Plate flanges (including Spacer & Blind) to spec A 182 & A240 for Normal, NACE& IBR Service, Rev 1, Dt. 15.03.2014 | Not Applicable | Issued by M/s RIL
3 | Drawing(s) | Not Applicable | Not Applicable | Not Applicable
4 | Procedure(s) | Not Applicable | Not Applicable | Not Applicable
5 | Datasheet(s) | Not Applicable | Not Applicable | Not Applicable
6 | Others (Specify) | Dimension Std: ASME B 16.48 | Not Applicable | Not Applicable

## Stages Witnessed
Stages Witnessed
ITP Sr. No. 2.5 : Selection of sample for product testing – Found to meet as per code & specification requirements.
ITP Sr. No. 2.6 : Product Tensile and Hardness Testing at NABL accredited lab on representative samples identified by TUV – Found to meet applicable code and specification requirements
ITP Sr. No. 2.7 : IGC Practice ‘E’ & Micro test for SS Items at NABL accredited lab on representative samples identified by TUV – Found to meet applicable code and specification requirements.
ITP Sr. No. 2.1 : Visual inspection (10% - Min. 01 No.) on randomly selected samples of offered line item - No injurious surface imperfections were observed.
ITP Sr. No. 2.2 : Dimensional inspection (10% - Min. 01 No.) on randomly selected samples of offered line item - Found to meet the standard requirements.
ITP Sr. No. 2.9 : PMI Testing (10% - Min. 01 No.) on randomly selected samples of offered line item – found to meet specification requirements.
ITP Sr. No. 2.12 : Pickling & Passivation (10% - Min. 01 No.) on randomly selected samples of offered line item – found to meet specification requirements.
ITP Sr. No. 2.13 : Marking and Stamping (10% - Min. 01 No.) on randomly selected samples checked of offered line item – found in order.
All measuring instruments/ equipment were verified for continued suitability for intended use, proper identification, calibration status, traceability to national standards & found satisfactory.

## Document reviewed
Document reviewed
ITP Sr. No. 1.1 : Copy of Raw material test certificate reviewed for its technical content only as declared by manufacturer and endorsed by SEC – Found to meet the applicable code requirement.
ITP Sr. No. 2.8 : Product chemical analysis lab test report – Found to meet the applicable code requirement.
WPS/PQR/WPQ record reviewed – found in order.
DP Test Report - Found in order.
ITP Sr. No. 2.9 - PMI Test reports - Found in order.
ITP Sr. No. 2.14 : Manufacturer test certificate No. SEC-RIL-PMD-FL-240565618-01 Dtd. 08.04.2023 declared by supplier - Found to meet material specification requirements.
Calibration certificates for measuring instruments – Found in order.

## Details of measuring instrument
Sr. No. | Detail of Equipment(s) / Instrument(s) | Range | ID | Validity till Date | Calibration Certificate Number | NABL / OTHER CERT. BODIES / NABL Traceability (type Yes wherever applicable) | NON-NABL (type Yes wherever applicable)
1 | Vernier Caliper | 0-300 mm | 1264520 | 05.03.2024 | MH/CL/23/03/218/NABL Date.06.03.2023 | Yes |  | Yes
2 | Measuring Tape | 0-3 Mtrs. | MT/3 Mtrs/01 | 16.10.2023 | MH/CL/22/10/471/NABL Date.17.10.2022 | Yes |  | No
3 | PMI Machine | - | Sr. No. 811679 | 12.09.2023 | Dtd. 13.09.2022 | Yes

## Areas of concerns
Areas Of Concern
None

## Pending Activities
Pending Activities from this visit
None

## Conclusion
Note: Data filled in this sheet will not upload in TIIMES
Non Conformities raised / Discrepancies observed during Inspection (If Any, Mention TUV India NCR Number ):
None
Identification of Inspected Item(s):
Above Inspected items double hard stamped as near manufacturer's marking.
Conclusion (Acceptable / Not Acceptable / Acceptance subject to):
Acceptable
IRN can be issued for PO Item numbers:
Expenses:
Remarks: