## Notes
Notes:
Data filled in General and conclusion Sections will not upload in TIIMES. Please use these sections to keep data ready for copy paste.
Data in Item Description columns of Accepted Quantity and cumulative Accepted quantity must be verified thoroughly before uploading in TIIMES.
Pending activity, Areas of concern & Details of measuring instruments sheets are applicable for IVR.
Select options from drop down list for unit of measurement (Item Description) & certifying body of measuring instruments (Details of measuring instruments).
Do not modify this format.
To start next row in cell itself use below shortcut: press 'alt + Enter' keys together. Alt + Enter

## General
Note: - Data filled in this sheet will not upload in TIIMES
Title | Details
Control Number
SAP number | 8117436886
Notification Number
Project Name & Location
Client Name
End User Name
DEC / PMC / EPC Name
DEC / PMC / EPC Number
Vendor Name
PO Number (Client PO on Vendor)
Sub Vendor
PO Number (Vendor PO on Sub Vendor)
Inspection Location
Inspection Date(s)

## Item Description
Po Item No. | Item Code | Item Description | Unit | Po Quantity | Offered Quantity | Accepted Quantity (Please verify thouroghly before using this Column for IRN) | Cumulative Accepted Quanitity (for IRN Only)
number
8 | 2002285273 | Gas turbine part : CO2 CYLINDER BANK ASEMBLY TO FIX 12 CYLINDERS, SL No,: FP/22/016,PART NO: IH030-12 - CS | number | 1 | 1 | 1 |  | meter
9 | 2002199592 | Gas turbine part : VALVE,MASTER,CO2,COMPLETE W/SOLENOID,PART NO: BIH001/DIN/EX, Batch & Serial No:10/22-6522 | number | 2 | 2 | 2 |  | km
10 | 2002135227 | Gas turbine part :VALVE,SLAVE,CO2;PN:BIH004/DIN, PART NO:BIH004/DIN, Batch & Serial No:04/22-0306 | number | 5 | 5 | 5 |  | meter (number)
11 | 2002285233 | Gas turbine part : NRV SUITABLE FOR CO2 MASTER CYLINDER,PART NO: IH018-R ,Batch & Serial No:FP/22/002 | number | 2 | 2 | 2 |  | km (number)
12 | 2000420430 | Gas Turbine Instrumentation Parts NRV,FOR SLAVE CYLINDER, PART NO: IH019 ,Batch & Serial No:FP/22/006 | number | 5 | 5 | 5 |  | each
13 | 2002045757 | Gas Turbine parts:HOSE,HIGH PRESSURE,DISCHARGE SZ:L 400MM,PART NO: BIH020, Batch No: INSAP–2-22 | number | 5 | 5 | 5 |  | Piece
14 | 2002135106 | Gas Turbine parts: HOSE,DISCHARGE,HIGH PRESSURE,CO2,350MM,PART NO: BIH021,Batch No: INSAP–6-22 | number | 2 | 2 | 2 |  | Test sample
15 | 2002135225 | Gas Turbine parts:HOSE,ACTUATION,CO2 HIGH PRESSURE,550MM, PART NO: BIH022,Batch No: INSAP–2-22 | number | 2 | 2 | 2 |  | AU - All Unit
16 | 2002135224 | Gas Turbine parts:HOSE,ACTUATION,CO2 HIGH PRESSURE,300MM,PART NO: BIH023 Batch No: INSAP–2-22 | number | 4 | 4 | 4 |  | lot
17 | 2001630022 | Control valves : VALVE MANIFOLD SAFETY,PART NO: IH138 Batch & Serial No:FP/21/004 | number | 1 | 1 | 1 |  | Set
18 | 2002285265 | Gas Turbine parts:EXPLOSION PROOF PRESSURE SWITCH ,PART NO: BIH144 , Batch & Serial No:90017ZBR | number | 1 | 1 | 1 |  | Running Meter
19 | 2002003502 | Fire and gas system parts: ASSY,LIMIT SWITCH; PN:IH006E R, PART NO: IH006E R ,Batch & Serial No:FP/22/16 | number | 10 | 10 | 10 |  | kg
20 | 2002285248 | Gas Turbine parts: CO2 DISCHARGE NOZZLE SMALL TYPE 1" , PART NO: IH011-M1"-SS304,Batch & Serial No:FP/22/07 | number | 2 | 2 | 2 |  | metric ton (tonne)
21 | 2002285282 | Gas Turbine parts: CO2 DISCHARGE NOZZLE SMALL TYPE 3/4", PART NO: IH011-M3/4"-SS304, Batch & Serial No:FP/22/08 | number | 2 | 2 | 2 |  | ton
22 | 2002285266 | Gas turbine parts: PILOT CO2 CYLINDERS FILLED WITH 4.5KGCO2, PART NO: BIH302-E-CS Cylinder Serial No: 550530, 550434,Valve Lot No:10/22-6522 | number | 2 | 2 | 2 |  | cubic millimetre
23 | 2002285283 | Gas turbine parts: DISTRIBUTOR ASSSEMBLY COMPLETE SET,PART NO: IH024/1-2 SV , Batch & Serial No: P/22/132 | number | 1 | 1 | 1 |  | cubic centimeter
24 | 2002285267 | Gas turbine parts: JOINING MANIFOLD COMPLETE SET,PART NO: IH136-2 Batch & Serial No: SA/22/001 | number | 1 | 1 | 1 |  | cubic meter
25 | 2002285284 | Gas turbine parts: HIGH PRESSURE ACTUATION HOSE,1000MM,PART NO: BIH381 ,Batch No: INSAP–7-22 | number | 4 | 4 | 4 |  | cubic inch
26 | 2002285287 | Gas turbine parts: HIGH PRESSURE ACTUATION HOSE,2000MM,PART NO: BIH454 ,Batch No: INSAP–8-20 | number | 2 | 2 | 2 |  | cubic foot
27 &6 | 2002288064 | Gas Turbine parts: CO2 CYLINDER BANK ASSEMBLY TO FIX 17 CYLINDER, & CO2 CYLINDER BANK ASEMBLY TO FIX 7 CYLINDERS, PART NO: IH030-24 D WD Batch & Serial No:FP/22/015 | number | 1 | 1 | 1 |  | mm
cm
in
foot
mile
yard
liter
kl
cl
ml
g
lb
oz
Sq. mm
Sq. cm
Sq. meter
Sq. in
Sq. foot

## Reference Documents
Sr. No. | Document Name | Client Document Number | Vendor Document Number | Approval Status
1 | PR/MR/ARM
2 | QAP/ITP/QCP | JT-J21P13-D1JBB-JL0001-MEC-P-00-A -BBD956-A05-0001-01 | ACSD2223BJ009-03 Rev 1 | Approved by RIL in Code 1
3 | Drawing(s) | Bill of material : JT-J21P13-D1JBB-JL0001-MEC-P-00-A -BBD956-F04-0001-01 | ACSD2223BJ009-11 Rev 1 | Approved by RIL in Code 1
4 | Procedure(s)
5 | Datasheet(s) | JT-J21P13-D1JBB-JL0001-MEC-P-00-A -BBD956-D03-0001-00 | ACSD2223BJ009-08 Rev 0 | Approved by RIL in Code 1
6 | Others (Specify)

## Stages Witnessed
Stages Witnessed
Visual inspection carriedout for all offered items -Found no visual defects,damages observed
Dimensional check carriedout for 100% of offered Items( Co2 Master valve, Slave valve,high pressure Discharge ,Actuation Hoses,Explosion proof Pressure switch,Pilot Co2 Cylinders,Co2 Cylinder bank assembly(17+7) & (6+6),NRV For Master Cylinder and Slave Cylinder,Manifold Safety valve,Discharge Nozles,Distributor asembly ,online monitor mechanical indicator and Joining manifold )as per approved Datasheet -Found acceptable and Inspection reports atteted for records.
Verified marking on each items ( Co2 Master valve, Slave valve,high pressure Discharge ,Actuation Hoses,Explosion proof Pressure switch,Pilot Co2 Cylinders,Co2 Cylinder bank assembly(17+7) & (6+6),NRV For Master Cylinder and Slave Cylinder,Manifold Safety valve,Discharge Nozles,Distributor asembly ,online monitor mechanical indicator and Joining manifold ) mfr Name/logo,Batch No /SL No as applicable, area classification ,IP class- Found inorder

## Document reviewed
Document reviewed
Reviewed Manufacturer Test certificates, compliance certificate for the offered items as per approve ddata sheet -Found acceptable
Reviewed CMIR/ Peso certificates for Pressure switch, Limit switches and pilot Cylinders-Found acceptable and attested for records.
Reviewed Manufacturer inspection report for all offered item - Found acceptable
Reviewed measuring instrument used for inspection and testing-Found inorder

## Details of measuring instrument
Sr. No. | Detail of Equipment(s) / Instrument(s) | Range | ID | Validity till Date | Calibration Certificate Number | NABL / OTHER CERT. BODIES / NABL Traceability (type Yes wherever applicable) | NON-NABL (type Yes wherever applicable)
1 | Veriner Caliper | 0 to 150mm | AC-15 | 21.02.2023 | CT22-82-1 | Yes |  | Yes
2 | Measuring tape | 0 to 7.5 Mtr | AC-33 | 08.09.2022 | CT21-298-5 | Yes |  | No
Type equation here.
"Type equation here."

## Areas of concerns
Areas Of Concern
Nil

## Pending Activities
Pending Activities from this visit
Nil

## Conclusion
Note: Data filled in this sheet will not upload in TIIMES
Non Conformities raised / Discrepancies observed during Inspection (If Any, Mention TUV India NCR Number ):
NIL
Identification of Inspected Item(s):
each item soft stameped thus for identification
Conclusion (Acceptable / Not Acceptable / Acceptance subject to):
Acceptable
IRN can be issued for PO Item numbers:
Expenses:
Remarks: