## Notes
Notes:
Data filled in General and conclusion Sections will not upload in TIIMES. Please use these sections to keep data ready for copy paste.
Data in Item Description columns of Accepted Quantity and cumulative Accepted quantity must be verified thoroughly before uploading in TIIMES.
Pending activity, Areas of concern & Details of measuring instruments sheets are applicable for IVR.
Select options from drop down list for unit of measurement (Item Description) & certifying body of measuring instruments (Details of measuring instruments).
Do not modify this format.
To start next row in cell itself use below shortcut: press 'alt + Enter' keys together. Alt + Enter

## General
Note: - Data filled in this sheet will not upload in TIIMES
Title | Details
Control Number
SAP number
Notification Number
Project Name & Location
Client Name
End User Name
DEC / PMC / EPC Name
DEC / PMC / EPC Number
Vendor Name
PO Number (Client PO on Vendor)
Sub Vendor
PO Number (Vendor PO on Sub Vendor)
Inspection Location
Inspection Date(s)

## Item Description
Po Item No. | Item Code | Item Description | Unit | Po Quantity | Offered Quantity | Accepted Quantity (Please verify thouroghly before using this Column for IRN) | Cumulative Accepted Quanitity (for IRN Only)
4 | Not Applicable | Austenitic stainless steel seamless tubes (Solution annealed pickled & passivated) as per ASTM A 312-21, SA 312 of ASME Sec. II Part-A Edition 2021, TP304/304L, EN 10216-5, TC-1, 1.4301/1.4307, D3/T3 & NACE MR 0175/ISO 15156-3: 2015, NACE MR 0103/ISO 17495-1: 2016, 2" NB X SCH 10S X 6.000meter long. | meter | 900meters | 468meters (78 Nos.) | 468meters (78 Nos.) | 468meters (78 Nos.) | number
7 | Not Applicable | Austenitic stainless steel seamless tubes (Solution annealed pickled & passivated) as per ASTM A 312-21, SA 312 of ASME Sec. II Part-A Edition 2021, TP304/304L, EN 10216-5, TC-1, 1.4301/1.4307, D3/T3 & NACE MR 0175/ISO 15156-3: 2015, NACE MR 0103/ISO 17495-1: 2016, 4" NB X SCH 10S X 6.000meter long. | meter | 150meters | 66meters (11 Nos.) | 66meters (11 Nos.) | 66meters (11 Nos.) | meter
8 | Not Applicable | Austenitic stainless steel seamless tubes (Solution annealed pickled & passivated) as per ASTM A 312-21, SA 312 of ASME Sec. II Part-A Edition 2021, TP304/304L, EN 10216-5, TC-1, 1.4301/1.4307, D3/T3 & NACE MR 0175/ISO 15156-3: 2015, NACE MR 0103/ISO 17495-1: 2016, 6" NB X SCH 10S X 6.000meter long. | meter | 120meters | 24meters (04 Nos.) | 24meters (04 Nos.) | 24meters (04 Nos.) | km
14 | Not Applicable | Austenitic stainless steel seamless tubes (Solution annealed pickled & passivated) as per ASTM A 312-21, SA 312 ASME Sec. II Part-A Edition 2021, TP316/316L, EN 10216-5, TC-1, 1.4401/1.4404, D3/T3 & NACE MR 0175/ISO 15156-3: 2015, NACE MR 0103/ISO 17495-1: 2016, NORSOK M630 MDS S01 Rev. 5, 1.1/2" NB X SCH 160 X 6.000 MTR LONG | meter | 90meters | 78meters (13 Nos.) | 78meters (13 Nos.) | 78meters (13 Nos.) | meter (number)
18 | Not Applicable | Austenitic stainless steel seamless tubes (Solution annealed pickled & passivated) as per ASTM A 312-21, SA 312 ASME Sec. II Part-A Edition 2021, TP316/316L, EN 10216-5, TC-1, 1.4401/1.4404, D3/T3 & NACE MR 0175/ISO 15156-3: 2015, NACE MR 0103/ISO 17495-1: 2016, NORSOK M630 MDS S01 Rev. 5, 4" NB X SCH 40S X 6.000 MTR LONG | meter | 780meters | 204meters (34 Nos.) | 204meters (34 Nos.) | 534meters (89 Nos.) | km (number)
each
Piece
Test sample
AU - All Unit
lot
Set
Running Meter
kg
metric ton (tonne)
ton
cubic millimetre
cubic centimeter
cubic meter
cubic inch
cubic foot
mm
cm
in
foot
mile
yard
liter
kl
cl
ml
g
lb
oz
Sq. mm
Sq. cm
Sq. meter
Sq. in
Sq. foot

## Reference Documents
Sr. No. | Document Name | Client Document Number | Vendor Document Number | Approval Status
1 | PR/MR/ARM | Not Applicable | Not Applicable | Not Applicable
2 | QAP/ITP/QCP | Not Applicable | GENERAL_ARCUS NEDERLAND_REV.05, Dated: 23.08.2021 | Approved by Arcus Nederland. B.V
3 | Drawing(s) | Not Applicable | Not Applicable | Not Applicable
4 | Procedure(s) | Not Applicable | Not Applicable | Not Applicable
5 | Datasheet(s) | Not Applicable | Not Applicable | Not Applicable
6 | Others (Specify) | Purchase specification: S-ASTM REV. 8, Dated: 23.08.2021 | Not Applicable | End User Document

## Stages Witnessed
Stages Witnessed
QAP Stage No-3 & 4 - Witnessed Sampling for Tensile test, Hardness test, Ring Expansion, Ring Tensile, Flattening test as per approved QAP & relevant specification -Found in order.
QAP Stage No-3 & 4 - Witnessed mechanical tests (Tensile, Ring Expansion, Ring Tensile, Flattening and Hardness Test) at manufacturer’s in-house testing facility on representative samples identified by TUV – found to meet the specification requirements.
QAP Stage No-6- Witnessed PMI Test for 10 % qty. tubes. – Found to meet the specification requirements.
QAP Stage No-12- Visual inspection carried out for 10 % qty. randomly selected tubes -No injurious surface defects observed.
QAP Stage No-13- Dimensions checked for 10% randomly selected tubes – Dimensions found within limit.
QAP Stage No-14- Verified Marking on tubes – Found in order.

## Document reviewed
Document reviewed
QAP stage no. 1: Reviewed copy of raw material test certificates as provided by supplier for chemical properties as per approved QAP - found in order.
QAP stage no. 2: Reviewed heat treatment (solution annealing) records as per approved QAP - found in order.
QAP Stage No-1 Reviewed Raw material test certificates as per approved QAP - Found to meet the specification requirements.
QAP Stage No-2 - Reviewed Solution Annealing Record- Found Satisfactory
QAP Stage No- 5 & 8, Reviewed Product analysis (Chemical test) report & IGC Practice “E” test report -Found in order
QAP Stage No- 9,10 & 11- Reviewed Eddy Current Test report & Hydrostatic test report -Found in order.
QAP Stage No- 15 Reviewed Manufacturer test certificates MTCPL/2022-23/0067A1 TO 0067A5, Dated 30.04.2022 - found in order.

## Details of measuring instrument
Sr. No. | Detail of Equipment(s) / Instrument(s) | Range | ID | Validity till Date | Calibration Certificate Number | NABL / OTHER CERT. BODIES / NABL Traceability (type Yes wherever applicable) | NON-NABL (type Yes wherever applicable)
1 | OUTSIDE MICROMETER | 0-25 MM | MM-41 | 2022-12-29 | NCQC-M/301221/14 Dated.03-01-2022 | Yes | No | Yes
2 | OUTSIDE MICROMETER | 25-50 MM | MM-07 | 2022-12-29 | NCQC-M/301221/16 Dated.03.01.2022 | Yes | No | No
3 | OUTSIDE MICROMETER | 50-75 MM | MM-22 | 2022-12-29 | NCQC-M/301221/17 Dated.03.01.2022 | Yes | No
4 | OUTSIDE MICROMETER | 75-100 | QMM-61 | 2022-05-07 | NCQC-M/080521/11 Dated. 10.05.2021 | Yes | No
5 | OUTSIDE MICROMETER | 100-125 | MM-38 | 2022-12-29 | NCQC-M/301221/20 Dated.03.01.2022 | Yes | No
6 | OUTSIDE MICROMETER | 125-150 | MM-39 | 2022-12-29 | NCQC-M/301221/21 Dated.03.01.2022 | Yes | No
7 | OUTSIDE MICROMETER | 150-300 | MM-12 | 2022-12-29 | NCQC-M/301221/22 Dated.03.01.2022 | Yes | No
8 | BALL POINT MICROMETER | 0-25 MM | QMB-01 | 2022-12-29 | NCQC-M/301221/07 Dated.03.01.2022 | Yes | No
9 | MEASURE TAPE | 0-30000 MM | M-MT-16 | 2022-05-07 | NCQC-M/080521/15, Dated. 10.05.2021 | Yes | No
10 | VERNIER CALIPER | 0-200 MM | VC-02 | 2022-12-29 | NCQC-M/301221/03 Dated.03.01.2022 | Yes | No
11 | UTM | 600KN | 2/2015-5500 | 2022-05-09 | KTS/N/010/1-3/21-22 Date.10.05.2021 | Yes | No
12 | Rockwell cum superficial Hardness Tester | 0-150 KGF | 07/06/009 | 2022-08-26 | KTS/N/099/2-2/21-22 Date.27.08.2021 | Yes | No
13 | PMI M/C. | -- | 813251 | 2022-07-07 | Tli/CAL/MTC/528 Date.08.07.2021 | No | Yes
14 | UTM | 400KN | 010-07/08 | 2022-08-26 | KTS/N/099/1-2/21-22 Date:-27.08.2021 | Yes | No

## Areas of concerns
Areas Of Concern
None

## Pending Activities
Pending Activities from this visit
None

## Conclusion
Note: Data filled in this sheet will not upload in TIIMES
Non Conformities raised / Discrepancies observed during Inspection (If Any, Mention TUV India NCR Number ):
Identification of Inspected Item(s):
Conclusion (Acceptable / Not Acceptable / Acceptance subject to):
IRN can be issued for PO Item numbers:
Expenses:
Remarks: