## Notes
Notes:
Data filled in General and conclusion Sections will not upload in TIIMES. Please use these sections to keep data ready for copy paste.
Data in Item Description columns of Accepted Quantity and cumulative Accepted quantity must be verified thoroughly before uploading in TIIMES.
Pending activity, Areas of concern & Details of measuring instruments sheets are applicable for IVR.
Select options from drop down list for unit of measurement (Item Description) & certifying body of measuring instruments (Details of measuring instruments).
Do not modify this format.
To start next row in cell itself use below shortcut: press 'alt + Enter' keys together. Alt + Enter

## General
Note: - Data filled in this sheet will not upload in TIIMES
Title | Details
Control Number
SAP number
Notification Number
Project Name & Location
Client Name
End User Name
DEC / PMC / EPC Name
DEC / PMC / EPC Number
Vendor Name
PO Number (Client PO on Vendor)
Sub Vendor
PO Number (Vendor PO on Sub Vendor)
Inspection Location
Inspection Date(s)

## Item Description
Po Item No. | Item Code | Item Description | Unit | Po Quantity | Offered Quantity | Accepted Quantity (Please verify thouroghly before using this Column for IRN) | Cumulative Accepted Quanitity (for IRN Only)
1 | 500204721133 | SS321 EXPANSION BELLOW FOR COAL FIRED HAG OUTLET, SIZE:- 1600NB X 500 MM LONG; SR No. 1 & 2 Size: Ø 1600 mm Type: Universal type tied Long: 500 mm Flue Gas Temperature: 600 Deg. Design Pressure:0.2 kg/cm2 Test Pressure: 0.3 kg/cm2 Axial Movement: ± 25 mm Lateral Movement: ± 10 mm Fatigue Life Cycle: Above 10000 cycles M.O.C "For Bellows:- SS 321 For Inner Sleeve:- SS 321 For Spool:- SS 321 For Fixed Flange:- IS 2062 For Lugs:- IS 2062" | number | 2 | 2 | Nil. Refer area of concern |  | number
meter
km
meter (number)
km (number)
each
Piece
Test sample
AU - All Unit
lot
Set
Running Meter
kg
metric ton (tonne)
ton
cubic millimetre
cubic centimeter
cubic meter
cubic inch
cubic foot
mm
cm
in
foot
mile
yard
liter
kl
cl
ml
g
lb
oz
Sq. mm
Sq. cm
Sq. meter
Sq. in
Sq. foot

## Reference Documents
Sr. No. | Document Name | Client Document Number | Vendor Document Number | Approval Status
1 | PR/MR/ARM | Not Applicable | Not Applicable | Not Applicable
2 | QAP/ITP/QCP | Not Applicable | 007/22-23-R-1, Dated 19.06.2022 | Approved by M/s.BEIL INFRASTRUCTURE
3 | Drawing(s) | Not Applicable | SEJB-8242-22-23-R-2 | Approved by M/s.BEIL INFRASTRUCTURE
4 | Procedure(s) | Not Applicable | Not Applicable | Not Applicable
5 | Datasheet(s) | Not Applicable | Not Applicable | Not Applicable
6 | Others (Specify) | Not Applicable | Not Applicable | Not Applicable

## Stages Witnessed
Stages Witnessed
QAP Stage No.C1; 1) For Sr No. 1 & 2 Visual inspection carried out in painted condition -No surface defects were observed. 2) For Sr No. 1, Dimensional inspection carried out- Found to meet the approved drawing requirement.
QAP Stage No.C2, for Sr No. 1 Air jet test inspection carried out for Flange to Bellow joints only at above 0.3 Kg/cm^2 (g) [Required : 0.3 Kg/cm^2 (g) ] and checked -No leakage detected by soap solution.
QAP Stage No. C3, For Sr. 1 & Sr.2 Painting inspection of Bellow carried out and visually checked for paint defect- Found free from paint defect like Runs, Sags, Pin holes, Bubbling, Cracking etc.

## Document reviewed
Document reviewed
QAP Stage No. A1 & A2;Reviewed Raw material lab test reports for bellow element and Sleeve for its technical content as declared by supplier and endorse by M/s. SEJM-Found to meet material specification requirement
QAP Stage No. B1 & B2, LPE report of bellow LS & forming portion- Found in order
Calibration record of testing and measuring instruments used for inspection-Found in order.

## Details of measuring instrument
Sr. No. | Detail of Equipment(s) / Instrument(s) | Range | ID | Validity till Date | Calibration Certificate Number | NABL / OTHER CERT. BODIES / NABL Traceability (type Yes wherever applicable) | NON-NABL (type Yes wherever applicable)
Yes
No

## Areas of concerns
Areas Of Concern

## Pending Activities
Pending Activities from this visit

## Conclusion
Note: Data filled in this sheet will not upload in TIIMES
Non Conformities raised / Discrepancies observed during Inspection (If Any, Mention TUV India NCR Number ):
Identification of Inspected Item(s):
Conclusion (Acceptable / Not Acceptable / Acceptance subject to):
IRN can be issued for PO Item numbers:
Expenses:
Remarks: