## Notes
Notes:
Data filled in General and conclusion Sections will not upload in TIIMES. Please use these sections to keep data ready for copy paste.
Data in Item Description columns of Accepted Quantity and cumulative Accepted quantity must be verified thoroughly before uploading in TIIMES.
Pending activity, Areas of concern & Details of measuring instruments sheets are applicable for IVR.
Select options from drop down list for unit of measurement (Item Description) & certifying body of measuring instruments (Details of measuring instruments).
Do not modify this format.
To start next row in cell itself use below shortcut: press 'alt + Enter' keys together. Alt + Enter

## General
Note: - Data filled in this sheet will not upload in TIIMES
Title | Details
Control Number
SAP number
Notification Number
Project Name & Location
Client Name
End User Name
DEC / PMC / EPC Name
DEC / PMC / EPC Number
Vendor Name
PO Number (Client PO on Vendor)
Sub Vendor
PO Number (Vendor PO on Sub Vendor)
Inspection Location
Inspection Date(s)

## Item Description
Po Item No. | Item Code | Item Description | Unit | Po Quantity | Offered Quantity | Accepted Quantity (Please verify thouroghly before using this Column for IRN) | Cumulative Accepted Quanitity (for IRN Only)
1 |  | 3 KL MSGL REACTOR.(Tag No.: R-4602,4604,4605) | number | 3 | 3 | Refer Conclusion |  | number
meter
km
meter (number)
km (number)
each
Piece
Test sample
AU - All Unit
lot
Set
Running Meter
kg
metric ton (tonne)
ton
cubic millimetre
cubic centimeter
cubic meter
cubic inch
cubic foot
mm
cm
in
foot
mile
yard
liter
kl
cl
ml
g
lb
oz
Sq. mm
Sq. cm
Sq. meter
Sq. in
Sq. foot

## Reference Documents
Sr. No. | Document Name | Client Document Number | Vendor Document Number | Approval Status
1 | PR/MR/ARM | Not Applicable | Not Applicable | Not Applicable
2 | QAP/ITP/QCP | Not Applicable | D-QCD-01 Rev.7 | HLE Standard QAP as mentioned in Approved Drawing
3 | Drawing(s) | Not Applicable | G-CE-300A-XXX/17818-19 Rev. 02 G-CE-300A-XXX/17820 Rev.02 | Approved by Client trough mail Dtd: 22.09.2021
4 | Procedure(s) | Not Applicable | Not Applicable | Not Applicable
5 | Datasheet(s) | Not Applicable | Not Applicable | Not Applicable
6 | Others (Specify) | Not Applicable | Not Applicable | Not Applicable

## Stages Witnessed
Stages Witnessed
QAP Sr. No.: 1.1 Hydro test of complete equipment Main shell , Jacket and BOV witnessed at a pressure above 6.0 Bar (g) [Required test pressure: 6.0 Bar (g)] in vertical condition for 30 minutes holding time- No leakage / no pressure drop observed during holding time.
QAP Sr.No.:1.2 Running trial of agitator assembly for 1 hour at atmosheric pressure with water filled up to working volume -Motor Current, RPM, Shaft run out near seal areas, Vibration and noise level , Temp raise of motor, Mdechanical Seal ,Bearing and Gear Box after 1 Hour running were checked & found to meet approved drawing and QAP requirement.
QAP Sr.No.:1.3(i) Glass lining spark test at 10 KV at accessible area inside reactor ,manhole cover and BOV - No spark were detected.Found Satisfactory.
QAP Sr.No. 1.3(ii) Glass lining thickness check at random spots for accessible area inside reactor ,manhole cover and BOV - Found to meet approved drawing & specification requirements. [1 to 2.2 mm (±0.2 mm)].
QAP Sr.No.2 Equipment visually checked for surface defect at accessible area iside and outside -Found free from injurious surface defect.
Verified nozzle position visually- Found as per drawing.
All measuring instruments/ equipment were verified for continued suitability for intended use, proper identification, calibration status, traceability to national standards & found satisfactory.

## Document reviewed
Document reviewed
Calibration record of measuring and testing equipments -Found in order.

## Details of measuring instrument
Sr. No. | Detail of Equipment(s) / Instrument(s) | Range | ID | Validity till Date | Calibration Certificate Number | NABL / OTHER CERT. BODIES / NABL Traceability (type Yes wherever applicable) | NON-NABL (type Yes wherever applicable)
1 | Pressure Gauge | 0-20 bar | N011.59-01766 | 28.01.2022 | PG-5666 DT:29.07.2021 | Yes |  | Yes
2 | Pressure Gauge | 0-21 Bar | N163.59-00805 | 11.04.2022 | 7888/N/2021 DT:11.10.2021 | Yes |  | No
3 | Pressure Gauge | 0-20 Bar | N011.59-01762 | 15.05.2022 | PG-6257 DT:16.11.2021 | Yes
4 | Pressure Gauge | 0-16 Bar | K012.59-01709 | 28.01.2022 | PG-5654 DT:29.07.2021 | Yes
5 | Pressure Gauge | 0-20 Bar | N011.59-01753 | 28.01.2022 | PG-5668 DT:29.07.2021 | Yes
6 | Pressure Gauge | 0-16 Bar | N163.59-00801 | 11.04.2022 | 7883/N/2021 DT:11.10.2021 | Yes
7 | Pressure Gauge | 0-20 Bar | N011.59-01755 | 15.03.2022 | PG-5663 DT:16.09.2021 | Yes
8 | Digital clamp meter |  | 180731221 | 24.05.2022 | 2246/E/2021 DT:24.05.2021 | Yes
9 | Digital techometer | 0-3000 rpm | S-1049886 | 24.06.2022 | 202110625-10311-4 DT:25.06.2021 | Yes
10 | Digital sound level meter | 35-130 db | 20180513287 | 24.05.2022 | 3345/N/2021 DT:24.05.2021 | Yes
11 | Infrared Thermometer | (-50) to 1150 degree | GH-2185723 | 05.03.2022 | CCS/7236/20-21 DT:08.03.2021 | Yes
12 | Plunger type dial gauge | 0-10 mm | DLA862 | 20.01.2022 | 571/N/2021 DT:20.01.2021 | Yes
13 | Spark tester | 0-20 kv | 20210723-2145 | 22.07.2022 | 20210723-2145-1 DT:23.07.2021 | Yes
14 | Digital coating thickness gauge | 0-1000 micron | 7574 | 20.02.2022 | 1473/N/2021 DT:20.02.2021 | Yes
15 | Digital vibration meter | 42 mm/Sec RMS Max | Model No. AVD-80 | 01.07.2022 | 20210702-10021-7 DT:02.07.2021 | No | Yes
16 | Pressure Gauge | 0-20 bar | M255.59-00630 | 15.03.2022 | PG-5967 DT:16.09.2021 | Yes
17 | Pressure Gauge | 0-20 bar | N163.59-00810 | 11.04.2022 | 7886/N/2021 DT:11.10.2021 | Yes

## Areas of concerns
Areas Of Concern
For Tag No.: R-4605 ; Bottom outlet valve not ready.Inspection of the same is balance.
Painting and finshing to be carried out as per drawing requirement.
02 Nos Sets for Asbestos free gaskets for all Nozzles including body flange and 10% Fasteners (Min.4 Nos Each Size) to be supplied as per drawing.

## Pending Activities
Pending Activities from this visit
For Tag No.: R-4605 ; Bottom outlet valve not ready.Inspection of the same is balance.

## Conclusion
Note: Data filled in this sheet will not upload in TIIMES
Non Conformities raised / Discrepancies observed during Inspection (If Any, Mention TUV India NCR Number ):
None
Identification of Inspected Item(s):
None
Conclusion (Acceptable / Not Acceptable / Acceptance subject to):
Acceptable
IRN can be issued for PO Item numbers:
Expenses:
Remarks: