## Notes
Notes:
Data filled in General and conclusion Sections will not upload in TIIMES. Please use these sections to keep data ready for copy paste.
Data in Item Description columns of Accepted Quantity and cumulative Accepted quantity must be verified thoroughly before uploading in TIIMES.
Pending activity, Areas of concern & Details of measuring instruments sheets are applicable for IVR.
Select options from drop down list for unit of measurement (Item Description) & certifying body of measuring instruments (Details of measuring instruments).
Do not modify this format.
To start next row in cell itself use below shortcut: press 'alt + Enter' keys together. Alt + Enter

## General
Note: - Data filled in this sheet will not upload in TIIMES
Title | Details
Control Number
SAP number
Notification Number
Project Name & Location
Client Name
End User Name
DEC / PMC / EPC Name
DEC / PMC / EPC Number
Vendor Name
PO Number (Client PO on Vendor)
Sub Vendor
PO Number (Vendor PO on Sub Vendor)
Inspection Location
Inspection Date(s)

## Item Description
Po Item No. | Item Code | Item Description | Unit | Po Quantity | Offered Quantity | Accepted Quantity (Please verify thouroghly before using this Column for IRN) | Cumulative Accepted Quanitity (for IRN Only)
1 | 998346 | Anode SACP, Magnesium (Low Potential), 80 mm Dia x 900 mm Length | number | 22 | 22 | 22 | 22 | number
2 | 998346 | Anode SACP, Magnesium (High Potential), 80 mm Dia x 900 mm Length | number | 5 | 5 | 5 | 5 | meter
3 | 998346 | Anode SACP Zinc, 800 mm Length x 60 mm Width x 60 mm Thickness | number | 27 | 27 | 27 | 27 | km
meter (number)
km (number)
each
Piece
Test sample
AU - All Unit
lot
Set
Running Meter
kg
metric ton (tonne)
ton
cubic millimetre
cubic centimeter
cubic meter
cubic inch
cubic foot
mm
cm
in
foot
mile
yard
liter
kl
cl
ml
g
lb
oz
Sq. mm
Sq. cm
Sq. meter
Sq. in
Sq. foot

## Reference Documents
Sr. No. | Document Name | Client Document Number | Vendor Document Number | Approval Status
1 | PR/MR/ARM | NA | NA | NA
2 | QAP/ITP/QCP | BSIN-CPJ21112-001-ITP | NA | Approved by M/s. Tractebel Enge
3 | Drawing(s) | BSIN-DR-CPJ21112-011, Rev.02, BSIN-DR-CPJ21112-012, Rev.02, BSIN-DR-CPJ21112-013, Rev.02 | NA | Approved by M/s. Tractebel Enge
4 | Procedure(s) | NA | NA | NA
5 | Datasheet(s) | BSIN-CPJ21112-001-MTL | NA | Approved by M/s. Tractebel Enge
6 | Others (Specify) | NA | NA | NA

## Stages Witnessed
Stages Witnessed
The following Points are witnessed as per QAP 10 % on randomly selected samples with the following identification no., SME-21-22-MH-104- 24,29,34,41 for Magnesium Anodes (Low Potential), SME-21-22-MH- 8 for Magnesium Anodes (High Potential) & SME-21-22-ZH-62- 12,20,29,34 for Zinc Anodes.
Witnessed the Visual check carried out 100 % for Longitudinal Cracks, Surface Defect & finishing found within the acceptable limits - found Satisfactory.
Witnessed the Dimensional Check for length, Width, Height & Weight carried on 10 % for on offered quantity & found within the acceptable limits - found Satisfactory.
Inspected the Destructive Testing (SME-21-22-MH-104- 44, SME-21-22-MH-105- 10, SME-21-22--ZH-62- 38) observation there is no slag inclusions in Magnesium anodes (Low Potential & High Potential) & Zinc Anodes - good bonding between the Anodes & insert - acceptable found ok.
Witnessed the Continuity check carried out 100 % for Magnesium anodes (Low Potential & High Potential) & Zinc Anodes - acceptable & found Satisfactory.
Witnessed the Open Circuit Potential for Magnesium anodes (Low Potential, High Potential) & Zinc anodes - within the acceptable limits & found Satisfactory.

## Document reviewed
Document reviewed
Radiography Test Report / film evaluated for one anode per Heat for an offered Magnesium anodes (Low Potential / SME-21-22-MH-104-6, High Potential / SME-21-22-MH-105-9) & Zinc Anodes / SME-21-22-ZH-62-11 - as per ITP & found satisfactory.
Chemical Composition Test results are reviewed for identification no. (SME-21-22-MH-104, SME-21-22-MH-105,SME-21-22-ZH-62) test report reviewed & found in order.
Electro Chemical test results are reviewed for Heat No. (SME-21-22-MH-104, SME-21-22-MH-105,SME-21-22-ZH-62) - found in order.
Manufacturer test reports are reviewed for Heat No. (SME-21-22-MH-104, SME-21-22-MH-105,SME-21-22-ZH-62) - found in order.

## Details of measuring instrument
Sr. No. | Detail of Equipment(s) / Instrument(s) | Range | ID | Validity till Date | Calibration Certificate Number | NABL / OTHER CERT. BODIES / NABL Traceability (type Yes wherever applicable) | NON-NABL (type Yes wherever applicable)
1 | Weighing Machine | 0 - 150 Kg | 267485 | 06.11.2021 | 1367 / 7, Dt: 06.11.2020 | No |  | Yes
2 | Vernier Caliper | 0 - 200 mm | FB202525 | 18.07.2022 | CC2101218 / 3, Dt: 19.07.2021 | Yes |  | No
3 | Measuring Tape | 0 - 3 Mtr | MT - 01 | 07.10.2021 | Tii201007-5-1, Dt: 07.10.2020 | Yes

## Areas of concerns
Areas Of Concern

## Pending Activities
Pending Activities from this visit

## Conclusion
Note: Data filled in this sheet will not upload in TIIMES
Non Conformities raised / Discrepancies observed during Inspection (If Any, Mention TUV India NCR Number ):
Identification of Inspected Item(s):
Conclusion (Acceptable / Not Acceptable / Acceptance subject to):
IRN can be issued for PO Item numbers:
Expenses:
Remarks: