## Notes
Notes:
Data filled in General and conclusion Sections will not upload in TIIMES. Please use these sections to keep data ready for copy paste.
Data in Item Description columns of Accepted Quantity and cumulative Accepted quantity must be verified thoroughly before uploading in TIIMES.
Pending activity, Areas of concern & Details of measuring instruments sheets are applicable for IVR.
Select options from drop down list for unit of measurement (Item Description) & certifying body of measuring instruments (Details of measuring instruments).
Do not modify this format.
To start next row in cell itself use below shortcut: press 'alt + Enter' keys together. Alt + Enter

## General
Note: - Data filled in this sheet will not upload in TIIMES
Title | Details
Control Number
SAP number
Notification Number
Project Name & Location
Client Name
End User Name
DEC / PMC / EPC Name
DEC / PMC / EPC Number
Vendor Name
PO Number (Client PO on Vendor)
Sub Vendor
PO Number (Vendor PO on Sub Vendor)
Inspection Location
Inspection Date(s)

## Item Description
Po Item No. | Item Code | Item Description | Unit | Po Quantity | Offered Quantity | Accepted Quantity (Please verify thouroghly before using this Column for IRN) | Cumulative Accepted Quanitity (for IRN Only)
150 | 423 | Commodity code :- EB3B51 Gate VALVE, Flangend ( RF ) MOC : ASTM A 216 Gr. WCB Size : 2" X 150 Class Tag No. : UNS213AB & VUW22OD Valve Sr. no.: D23B058 TO D23B059 | Piece | 2 | 2 | 2 | 2 | number
160 | 423 | Commodity code :- EB3B51 Gate VALVE, Flangend ( RF ) MOC : ASTM A 216 Gr. WCB Size : 2" X 150 Class Tag No. : UNS220F , UNS220G , UNS220J , VAG030I & VIG210A Valve Sr. no.: D23B012 TO D23B016 | Piece | 5 | 5 | 5 | 5 | meter
170 | 423 | Commodity code :- EH3E50 Gate Valve , End connection - SWE MOC : ASTM A105 Size : 1" X 800 Class Tag No. : VCW202N , VCHW205U , VCHW201E , SPARE Valve Sr. no.:G23B0273 TO G23B0276 | Piece | 4 | 4 | 4 | 4 | km
180 | 423 | Commodity code :- EH3E50 Gate Valve, End connection - SWE MOC : ASTM A105 Size : 1/2" X 800 Class Tag No. : VNS213Y , VNS213X, VNS213W, VNS213V, VNS213U, VNS213T, VNS213S, VNS213R, VNS213Q, VNS213P, VNS213O, VNS213N, VNS213M, VCHW205B, VCW201, VUW220B, VCW202L, VCW202G, VCW202E, VCW202W, VCW202Y, VCW202U, VCW202V, VCW202R, VCW202Z, VCW202I, VCW013B, VCW011B, VCW201K, VCW201F, VCW201H, VCW201J, VCW201I, VPT6068 ,VCW012B, VCW010B, VCW201B, VCW201D, VGAN190V, VGAN190W, VGAN190P, VGAN190U, SPARE , SPARE Valve Sr. no.:G23B0288 TO G23B0331 | Piece | 44 | 44 | 44 | 44
190 | 423 | Commodity code :- EH3G50 Gate Valve , End connection - one side SE NPT ( F ) and other side SWE MOC : ASTM A105 Size : 1" X 800 Class Tag No. : VC01, VC02, VC03, VC04, VC05, VC06, VC07, VC08, VC09, VC10 , SPARE Valve Sr. no.:G23B0277 TO G23B0287 | Piece | 11 | 11 | 11 | 11 | meter (number)
250 | 423 | Commodity code :- FH3E50 Globe Valve , End connection - SWE MOC : ASTM A105 Size : 1" X 800 Class Tag No. : VCHW205D , VIG040A , VIG041A , VIG023A, VCHW021B, VCHW021D, NA, SPARE Valve Sr. no.:G23B0251 TO G23B0258 | Piece | 8 | 8 | 8 | 8 | km (number)
260 | 423 | Commodity code :- FH3E50 Globe Valve, End connection - SWE MOC : ASTM A 105 Size : 1/2" X 800 Class Tag No. : VIG083A, VIG064A, VIG076A, NA, SPARE Valve Sr. no.:G23B0259 TO G23B0263 | Piece | 5 | 5 | 5 | 5 | each
270 | 423 | Commodity code :- FH3E50 Globe Valve, End connection - SWE MOC : ASTM A 105 Size : 1.1/2" X 800 Class Tag No. : VNS213AG, VNS213AH, VNS213AI, VNS213AJ, VNS213AK, VNS213AF, VNS213AN, VNS213AO, SPARE Valve Sr. no.:G23B0264 TO G23B0272 | Piece | 9 | 9 | 9 | 9 | Piece
280 | 423 | Commodity code :- DH3E50 Lift Check Valve, End connection - SWE MOC : ASTM A 105 Size : 1/2" X 800 Class Tag No. : CVNS213A, CVNS213B, CVNS213C . Valve Sr. no.:G23B0248 TO G23B0250 | Piece | 3 | 3 | 3 | 3 | Test sample
300 | 423 | Commodity code :- EH3G50 Gate Valve , End connection - one side SE NPT ( F ) and other side SWE MOC : ASTM A105 Size : 1/2" X 800 Class Tag No. : VNS213A, VNS213B, VNS213C, VNS213D, VNS213AL, VPG9565, VPG9564, VPG9563, VPG9562, VPG9561, VPT6080A, VPI6061A, VPI6062A, VPT7067A, VPT7068A, VPT9005B, SPARE, SPARE Valve Sr. no.:G23B0332 TO G23B0349 | Piece | 18 | 18 | 18 | 18 | AU - All Unit
lot
Set
Running Meter
kg
metric ton (tonne)
ton
cubic millimetre
cubic centimeter
cubic meter
cubic inch
cubic foot
mm
cm
in
foot
mile
yard
liter
kl
cl
ml
g
lb
oz
Sq. mm
Sq. cm
Sq. meter
Sq. in
Sq. foot

## Reference Documents
Sr. No. | Document Name | Client Document Number | Vendor Document Number | Approval Status
1 | PR/MR/ARM | Not Applicable | Not Applicable | Not Applicable
2 | QAP/ITP/QCP | 12173-PP-005-502D730 , REV.01 | OIL/ITP/220070-001, REV.01, Dated: 05.11.2022 | Approved By Air Liquide in Code-A on Dtd : 20.11.2022 by Mr. Kalyan Chakravarthi
3 | Drawing(s) | 12173-PP-005-502D400 , Rev.03 | 1. GTGA-220070-001 , Rev.02 2. GTGA-220070-002 , Rev.02 3. GBGA-220070-004 , Rev.02 4. LCGA-220070-006 , Rev.03 5. GTGA-220156-001 , Rev.00 | Approved By Air Liquide in Code-A on Dtd : 10.01.2023 by Mr. Prashant Ku Behra
4 | Procedure(s) | Not Applicable | Not Applicable | Not Applicable
5 | Datasheet(s) | Not Applicable | Not Applicable | Not Applicable
6 | Others (Specify) | 1. CLEANING AND CLEANLINESS OF EQUIPMENT AND PIPING :- G-GS-4-0-1 , Rev.01 2. GENERAL SPECIFICATION :- G-GS-5-4-1 Rev. 0 | Not Applicable | Client Document

## Stages Witnessed
Stages Witnessed
ITP Stage No 3.1: Visual inspection carried out for surface condition on 100 % Qty of Valves for each PO. Line items as per approved ITP & Drawing – Found free of injurious defects.
ITP Stage No 3.1: Dimension check on 10 % Randomly selected Valves for each PO. Line items as per approved ITP & Drawing - observed dimension found to meet the Approved Drawings requirements.
ITP Stage No 3.2: Witnessed Hydrostatic Shell test on 10 % random selected Gate valves , Globe valves & Lift check Valves as per approved ITP & drawing - No Leakage / No Pressure drop observed after holding time during inspection.
ITP Stage No 3.3: Witnessed Hydrostatic back Seat test on 10 % random selected Gate valves & Globe valves as per approved ITP & drawing - No Leakage / No Pressure drop observed after holding time during inspection.
ITP Stage No 3.4: Witnessed Hydrostatic Seat test on 10 % random selectedGate valves , Globe valves & Lift check Valves as per approved ITP & drawing - No Leakage / No Pressure drop observed after holding time during inspection.
ITP Stage No 3.5: Witnessed Pneumatic (Air) Seat test on 10 % random selected Gate valves & Globe valves as per approved ITP & drawing - No Leakage / No Pressure drop observed after holding time during inspection.
ITP Stage No 3.6: Witnessed PMI Test on 10 % Randomly selected Valves for each PO. Line items on accesible Parts ( Aloy steel / Stainless steel ) as per approved ITP & drawing – observed chemical elements results confirming the grade.
ITP Stage No 4.1: After primer coat (Inorganic Zinc Silicate) Visual & Final Paint Thickness (DFT) checked at random location on 10% randomly selected Qty. of Valves from offered each PO line item of carbon steel valves as per approved ITP , Drawing , Project specification – Found acceptable.
ITP Stage No 4.3: Marking checked on valve & Tag verified on random selected 10% Qty. of valves for each PO. Line items as per approved ITP , Drawing , Project specification – Found to meet ITP & drawing requirement.
All measuring instruments/ equipment were verified for continued suitability for intended use, proper identification, calibration status, traceability to national standards & found satisfactory.

## Document reviewed
Document reviewed
ITP Stage No.1.1 : Reviewed Raw material test certificates ( EN 1024 Type3.1 ) as declared by vendor for Body & Bonnet / Cover with reference to approved drawing ,ITP & relevant standards – Found to meet the applicable standards requirements
ITP Stage No.1.3 : Reviewed Raw material test certificates ( EN 1024 Type3.1 ) as declared by vendor for wedge / Disc with reference to approved drawing ,ITP & relevant standards – Found to meet the applicable standards requirements
ITP Stage No.1.4 : Reviewed Raw material test certificates ( EN 1024 Type3.1 ) as declared by vendor for Stem with reference to approved drawing ,ITP & relevant standards – Found to meet the applicable standards requirements
ITP Stage No.1.5 : Reviewed Raw material test certificates ( EN 1024 Type2.1 ) as declared by vendor for gasket with reference to approved drawing ,ITP & relevant standards – Found to meet the applicable standards requirements
ITP Stage No.1.5 : Reviewed Raw material test certificates ( EN 1024 Type3.1 ) as declared by vendor for Fastner with reference to approved drawing ,ITP & relevant standards – Found to meet the applicable standards requirements
ITP Stage No.2.1 : Reviewed Internal Dye Penetrant test reports for Hard Facing / Stellited on wedge & Seat ring as per approved drawing , ITP & relevant standards – Found to meet the applicable standards requirements.
Reviewed calibration certificates of measuring instrument & Pressure gauges - Found in order to have valid calibration for intended use.
ITP Stage No.5.1 : Reviewed Manufacturer Final test certificates ( EN 10204 Type 3.1 ) TC No. SO/220156/2225052 ,SO/220156/2225088 Dated. 22.02.2023 , SO/220156/2225576 , SO/220156/2225617 ,SO/220156/2225579 ,SO/220156/2225623 ,SO/220156/2225639 ,SO/220156/2225798 ,SO/220156/2225841 ,SO/220156/2225827 , Dated. 27.02.2023 –Found to meet ITP & specification requirement

## Details of measuring instrument
Sr. No. | Detail of Equipment(s) / Instrument(s) | Range | ID | Validity till Date | Calibration Certificate Number | NABL / OTHER CERT. BODIES / NABL Traceability (type Yes wherever applicable) | NON-NABL (type Yes wherever applicable)
1 | Pressure Gauge | 0-400 Kg/cm2 | 212355-53-5 | 02.04.2023 | NCQC-MO/030123/04 , Dated. 04.01.2023 | Yes |  | Yes
2 | Pressure Gauge | 0-10 Kg/cm2 | 17GA-2914 | 02.04.2023 | NCQC-MO/030123/56 , Dated. 04.01.2023 | Yes |  | No
3 | Vernier Calliper | 0-300 mm | J120113682 | 23.02.2023 | NCQC-M/240222/14 , Dated. 25.02.2022 | Yes
4 | PMI Machine |  | 500N3640 | 17.08.2023 | BISPL/22-23/18 , Dated. 18.08.2022 |  | Yes
5 | Tapper Thread Plug Gauge | 1/2"-14 NPT | TPG-07 | 15.06.2023 | NCQC-M/160622/009 , Dated. 17.06.2022 | Yes
6 | Tapper Thread Plug Gauge | 1/2"-11.1/2 HIP | OL/PG/05 | 26.08.2023 | NCQC-M/270822/11 , Dated. 27.08.2022 | Yes

## Areas of concerns
Areas Of Concern
NONE

## Pending Activities
Pending Activities from this visit
ITP Stage No 1.1 to 1.6 : Incoming raw material test certificate review balance for ( PO. Line item - 00250, 00260, 00270, 00280 & 00300 ) as per approved ITP & drawing & project specification - These all documents Balance to offer from vendor side in this visit
ITP Stage No 4.1 : Final DFT mesurment of carbon steel offered valves ( PO. Line item -00170 , 00180 , 00190, 00250, 00260, 00270, 00280 & 00300 )as per approved ITP & drawing & project specification - Balance to offer from vendor side due to painting not done by vendor in this visit .
ITP Stage No 4.3 : Verification of marking and tagging of carbon steel offered valves ( PO. Line item -00170 , 00180 , 00190, 00250, 00260, 00270, 00280 & 00300 ) as per approved ITP & drawing & project specification - Balance to offer from vendor side due to marking & Tagging not done by vendor in this visit .
ITP Stage No 5.1 : IRN ( Inspection release note ) will be issued after completion / acceptance of above as mentioned balance activities in upcomming vist

## Conclusion
Note: Data filled in this sheet will not upload in TIIMES
Non Conformities raised / Discrepancies observed during Inspection (If Any, Mention TUV India NCR Number ):
Identification of Inspected Item(s):
10% Witnessed Valve identified with hard [Double] and balance are hard [Single] Stamp as “ “ Near valve serial No.
Conclusion (Acceptable / Not Acceptable / Acceptance subject to):
IRN can be issued for PO Item numbers:
Expenses:
Remarks: