## Notes
Notes:
Data filled in General and conclusion Sections will not upload in TIIMES. Please use these sections to keep data ready for copy paste.
Data in Item Description columns of Accepted Quantity and cumulative Accepted quantity must be verified thoroughly before uploading in TIIMES.
Pending activity, Areas of concern & Details of measuring instruments sheets are applicable for IVR.
Select options from drop down list for unit of measurement (Item Description) & certifying body of measuring instruments (Details of measuring instruments).
Do not modify this format.
To start next row in cell itself use below shortcut: press 'alt + Enter' keys together. Alt + Enter

## General
Note: - Data filled in this sheet will not upload in TIIMES
Title | Details
Control Number
SAP number
Notification Number
Project Name & Location
Client Name
End User Name
DEC / PMC / EPC Name
DEC / PMC / EPC Number
Vendor Name
PO Number (Client PO on Vendor)
Sub Vendor
PO Number (Vendor PO on Sub Vendor)
Inspection Location
Inspection Date(s)

## Item Description
Po Item No. | Item Code | Item Description | Unit | Po Quantity | Offered Quantity | Accepted Quantity (Please verify thouroghly before using this Column for IRN) | Cumulative Accepted Quanitity (for IRN Only)
1 | 2001331977 WFVG0G0A | SS, SEAMLESS, ELBOW 45° LR, BW, ASME B16.9, ASTM A403 GR. WP304L-S, SIZE 3" X SCH 40S. | number | 2 | 2 | 2 | 2 | number
2 | 2001319743 WNVG0G0D | SS, SEAMLESS, ELBOW 90° LR, BW, ASME B16.9, ASTM A403 GR. WP304L-S, SIZE 4" X SCH 40S, R=1.5D. | number | 4 | 4 | 4 | 4 | meter
3 | 2001319748 WNVG0G0D | SS, SEAMLESS, ELBOW 90° LR, BW, ASME B16.9, ASTM A403 GR. WP304L-S, SIZE 6" X SCH 40S, R=1.5D. | number | 4 | 4 | 4 | 4 | km
4 | 2000249880 WNWC0G0D | SS, SEAMLESS, ELBOW 90° LR, BW, ASME B16.9, ASTM A403 GR. WP316L-S, SIZE 3" X SCH 40S, R=1.5D. | number | 6 | 6 | 6 | 6 | meter (number)
5 | 2001319740 WTVG0G0E | SS, SEAMLESS, EQUAL TEE, BW, ASME B16.9, ASTM A403 GR. WP304L-S, SIZE 6" X SCH 40S. | number | 1 | 1 | 1 | 1 | km (number)
each
Piece
Test sample
AU - All Unit
lot
Set
Running Meter
kg
metric ton (tonne)
ton
cubic millimetre
cubic centimeter
cubic meter
cubic inch
cubic foot
mm
cm
in
foot
mile
yard
liter
kl
cl
ml
g
lb
oz
Sq. mm
Sq. cm
Sq. meter
Sq. in
Sq. foot

## Reference Documents
Sr. No. | Document Name | Client Document Number | Vendor Document Number | Approval Status
1 | PR/MR/ARM | 10080-1-SS-PP-004 Part -II Rev.02 & 10080-1-SS-PP-018 | Not Applicable | Issued by M/s RIL
2 | QAP/ITP/QCP | Annexure­9A_ITP for SS Forged & Seamless Fittings to A182, A403 for Normal & NACE, Rev.3, Dtd. 28.11.2016 (for SS Items) | Not Applicable | Approved by M/s RIL
3 | Drawing(s) | Not Applicable | Not Applicable | Not Applicable
4 | Procedure(s) | Not Applicable | Not Applicable | Not Applicable
5 | Datasheet(s) | Not Applicable | Not Applicable | Not Applicable
6 | Others (Specify) | Not Applicable | Not Applicable | Not Applicable

## Stages Witnessed
Stages Witnessed
QAP Sr. No. 2.1; Visual inspection (10 %) of offered lot of each line item - No injurious surface imperfections were observed.
QAP Sr.No.2.2; Product sample identified - Found to meet specification requirements.
QAP Sr. No. 2.3; Dimensional inspection for 10% Qty. - Found to meet the code and standard requirements.
QAP Sr. No. 2.4; Thickness checked by ultrasonic thickness gauge at Tee branch area (10% - Min. 01 No.) for randomly selected samples from offered lot of each line item - Found to meet the code and standard requirement
QAP Sr. No. 2.6; Mechanical testing, and Hardness test at NABL accredited lab on representative sample identified by TUV- Found to meet the standard / specification requirement.
QAP Sr. No. 2.8; Penetrant test 10% on bevel ends & full body surface area of Tee – No surface indication were observed
QAP Sr. No. 2.9; IGC Pr. E Test at NABL accredited lab on representative samples identified by TUV – found to meet the specification requirements.
QAP Sr. No. 2.10; PMI test on 10 % Qty.– Found to meet the applicable code and specification requirement.
QAP Sr. No. 2.11; Pickling and passivation 10% Qty. cheked - Found to meet the specification requirement.
QAP Sr. No. 2.13; Marking & stamping verified 10% Qty. – Found in order.
All measuring instruments/ equipment were verified for continued suitability for intended use, proper identification, calibration status, traceability to national standards & found satisfactory.

## Document reviewed
Document reviewed
QAP Sr. No. 1.1; Raw material test certificates reviewed for its technical content only as declared by manufacturer and endorsed by M/s. Topaz Piping Industries - Found to meet the applicable code and project specification requirements.
QAP Sr. No. 2.5; Heat Treatment Charts/reports - Found to meet the applicable code requirements.
QAP Sr. No. 2.7; Product Chemical check test reports as per approved QAP requirement- Found to meet the specification requirements.
QAP Sr. No. 2.12; Internal test report, Calibration reports & type test report (earlier Qualified in witness of TPIA) of fittings - Found to meet the code specification requirement.
QAP Sr. No. 2.14; Manufacturer’s TC.NO: 8061/23-24, R.0 & 8062/23-24, R.0 Dated 06.05.2023 - Found to meet the material specification requirements.
Internal test/inspection reports, Calibration reports & pre-qualification type test report (earlier Qualified in witness of TPIA) of fittings - Found to meet the code specification requirement.

## Details of measuring instrument
Sr. No. | Detail of Equipment(s) / Instrument(s) | Range | ID | Validity till Date | Calibration Certificate Number | NABL / OTHER CERT. BODIES / NABL Traceability (type Yes wherever applicable) | NON-NABL (type Yes wherever applicable)
1 | Measuring Tape | 0-5 Mtr | MT/3Mtrs/01 | 05.02.2024 | MH/CL/23/02/126/NABL, Dtd:06.02.2023 | Yes |  | Yes
2 | Digital Ultrasonic Thickness Gauge | 2 to 200 mm | EDISON-1/ Sr. No. 6924-9140 | 21.12.2023 | MH/CL/22/12/626/NABL, Dtd:22.12.2022 | Yes |  | No
3 | Portable Hardness Tester | --- | PHT-01 | 15.12.2023 | MH/CL/22/12/161, Dtd:16.12.2022 | Yes
4 | Alloy Analyzer | --- | JC975 | 24.11.2023 | MH/CL/22/11/121, Dtd:26.11.2022 | Yes

## Areas of concerns
Areas Of Concern
REMARKS:-- Photographs are not allowed by Vendor during inspection.

## Pending Activities
Pending Activities from this visit

## Conclusion
Note: Data filled in this sheet will not upload in TIIMES
Non Conformities raised / Discrepancies observed during Inspection (If Any, Mention TUV India NCR Number ):
None
Identification of Inspected Item(s):
Inspected 100% stamped (Witnessed double & rest Single ) as “ ” near manufacturers marking
Conclusion (Acceptable / Not Acceptable / Acceptance subject to):
Acceptable
IRN can be issued for PO Item numbers:
Expenses:
Remarks: