## Notes
Notes:
Data filled in General and conclusion Sections will not upload in TIIMES. Please use these sections to keep data ready for copy paste.
Data in Item Description columns of Accepted Quantity and cumulative Accepted quantity must be verified thoroughly before uploading in TIIMES.
Pending activity, Areas of concern & Details of measuring instruments sheets are applicable for IVR.
Select options from drop down list for unit of measurement (Item Description) & certifying body of measuring instruments (Details of measuring instruments).
Do not modify this format.
To start next row in cell itself use below shortcut: press 'alt + Enter' keys together. Alt + Enter

## General
Note: - Data filled in this sheet will not upload in TIIMES
Title | Details
Control Number
SAP number
Notification Number
Project Name & Location
Client Name
End User Name
DEC / PMC / EPC Name
DEC / PMC / EPC Number
Vendor Name
PO Number (Client PO on Vendor) | 21000121-OQ-10157 Dated: 22.04.2021
Sub Vendor
PO Number (Vendor PO on Sub Vendor)
Inspection Location
Inspection Date(s)

## Item Description
Po Item No. | Item Code | Item Description | Unit | Po Quantity | Offered Quantity | Accepted Quantity (Please verify thouroghly before using this Column for IRN) | Cumulative Accepted Quanitity (for IRN Only)
1 | 2200228605 | 36kV, 400A, 25kA/3swec, Outdoor, 3 Pole Off-Load isolator Serial Nos:SEISO230422287-1 to SEISO230422287-8 | number | 152 | 8 (10% Randomly Witnessed 1no) | 8 | 8 | number
2 | 9100093661 | 36kV, 1250A, 26.3kA/3swec, Outdoor, Solid Dielectric Insulated, 3 Pole Gang Operated, Vaccum Circuit Breaker with Permanent Magnetic Actuator Operating Mechanism Serial Nos: SEPMA230422287-1 to SEPMA230422287-8 | number | 152 | 8 (10% Randomly Witnessed 1no) | 8 | 8 | meter
5 | 2200028005 | 1100V Grade, 24c x 1.5 sq.mm Armoured Copper Control Cable between VCB and Control & Relay Panel, with Plug & Socket at Control Panel end, for VCB/CT Signals & Commands, Make: KEI | meter | 760 | 40 (10% Randomly Witnessed 5meters) | 40 | 40 | km
6 | 9100106626 | 1100V Grade, 10c x 1.5 sq.mm Armoured Copper Control Cable between Isolator and Control & Relay Panel, with Plug & Socket at Control Panel end, for Isolator signals , Make: KEI | meter | 1064 | 56 (10% Randomly Witnessed 7meters) | 56 | 56 | meter (number)
11 | 9100105651 | Control and Relay Panel for PMA VCB, Aux Supply: 24VDC / 230V AC Serial Nos: SECRP230422287-1 to SECRP230422287-8 | lot | 152 | 8 (10% Randomly Witnessed 1no) | 8 | 8 | km (number)
13 | 2200228659 | 1100V Grade, 24c x 1.5 sq.mm Armoured Copper Control Cable Glands Make: Trinity | each | 304 | (10% Randomly Witnessed 2nos) | 16 | 16 | each
14 | 2200228606 | 1100V Grade, 10c x 1.5 sq.mm Armoured Copper Control Cable Glands Make: Trinity | each | 304 | (10% Randomly Witnessed 2nos) | 16 | 16 | Piece
19 | 9100105403 | 1100V Grade, 24c x 1.5 sq.mm Armoured Copper Control Cable lugs Make: 3D | each | 7296 | (10% Randomly Witnessed 48nos) | 384 | 384 | Test sample
20 | 9100106625 | 1100V Grade, 10c x 1.5 sq.mm Armoured Copper Control Cable Make: 3D | each | 3040 | (10% Randomly Witnessed 20nos) | 160 | 160 | AU - All Unit
lot
Set
Running Meter
kg
metric ton (tonne)
ton
cubic millimetre
cubic centimeter
cubic meter
cubic inch
cubic foot
mm
cm
in
foot
mile
yard
liter
kl
cl
ml
g
lb
oz
Sq. mm
Sq. cm
Sq. meter
Sq. in
Sq. foot

## Reference Documents
Sr. No. | Document Name | Client Document Number | Vendor Document Number | Approval Status
1 | PR/MR/ARM | Not Applicable | Not Applicable | Not Applicable
2 | QAP/ITP/QCP | PMA and Relay: SWE/MQP/01 Rev.1 & Isolator: SWE/MQP/12 Rev.1 | Not Applicable | CAT-B, Approved with Comments by M/s.JSW & CAT-A, Approved by M/s.JSW
3 | Drawing(s) | SWE-36PMA-JSW-SND-LD-R1 | Not Applicable | Approved by M/s.FICHTNER, Dated: 21.03.2023
4 | Procedure(s) | Not Applicable | Not Applicable | Not Applicable
5 | Datasheet(s) | Not Applicable | Not Applicable | Not Applicable
6 | Others (Specify) | Not Applicable | Not Applicable | Not Applicable

## Stages Witnessed
Stages Witnessed
For Offered PMA VCB, Control and relay panel, Isolator as per QAP No: SWE/MQP/01 Rev.1 & SWE/MQP/12 Rev.1 Randomly witnessed 10% selected serial nos are: SEPMA230422287-5, SECRP230422287-5 & SEISO230422287-5
PMA VCB
100% Visual Inspection carried out the offered items - Found in order
Pain shade (RAL 7035) and Coating Thickness measured found above 90 Microns - Found Acceptable
General Arrangement, Earthing provision, Sheet Steel Thickness and Creepage distance of bushing insulators verfied - Found Acceptable
PMA VCB and terminal connectors overall dimensions checked as approved GA drawing - Found Acceptable
Verification of Components identification marking/ labels & Name plate details checked - Found Acceptable
Mechanical/Electrical Operations of PMA VCB Opening and closing, capacitor charging checked - Found Acceptable
Contact Resistance main circuits of PMA VCB checked - Found Acceptable
Opening and closing timings of PMA VCB - Found Acceptable
Functional and Tightness check of PMA VCB - Found Acceptable
High Voltage test on PMA VCB Open condition (80kV)/ VCB closed condition (70kV) for 1minute - Found withstood
Insulation Resistance for Main circuits and Auxillary circuit before & after HV Test - Found Acceptable
Isolator
100% Visual Inspection carried out the offered items - Found in order
Pain shade (RAL 7035) and Coating Thickness measured found above 90 Microns - Found Acceptable
General Arrangement, Earthing provision, Sheet Steel Thickness and Creepage distance of insulators verfied - Found Acceptable
Isolator and terminal connectors overall dimensions checked as approved GA drawing - Found Acceptable
Verification of Components identification marking/ labels & Name plate details checked - Found Acceptable
Mechanical Operations of isolator Opening and closing checked - Found Acceptable
Contact Resistance main circuits of isolator checked - Found Acceptable
High Voltage test on Isolator closed condition (70kV)/ VCB Open condition (80kV) for 1minute - Found withstood
Insulation Resistance for Main circuits and Auxillary circuit before & after HV Test - Found Acceptable
Control and Relay Panel
100% Visual Inspection carried out the offered items - Found in order
Overall dimensions checked as approved GA drawing - Found Acceptable
Pain shade (RAL 7035) and Coating Thickness measured found above 90 Microns - Found Acceptable
Surface Finish, Door alignment Fixing of Gasket checked - Found Acceptable
Mounting & Proper Fixing of all components checked - Found Acceptable
Wiring arrangement & Ferruling check as per scheme - Found Acceptable
Verification of Components identification marking/ labels & Name plate details checked - Found Acceptable
Cable entry and gland plate thickness, Earth bus bar dimension checked - Found Acceptable
BOM verification for Quantity, Make & Ratings - Found Acceptable
General Asthetics, Functional and interlock checked - Found Acceptable
High Voltage test on Control Circuit (1.0 kV) - Found withstood
Insulation Resistance for control circuit before & after HV Test - Found Acceptable
All measuring instruments/ equipment were verified for continued suitability for intended use, proper identification, calibration status, traceability to national standards & found satisfactory

## Document reviewed
Document reviewed
Reviewed Acceptance test for PMA VCB, relay panel and Isolators - Found in order.
Reviewed the Internal Routine test reports of PMA VCB, Isolators - Found in order
Reviewed the Material test certificates VCB interrupter, Auxillary Switches, Insualtors, Voltmeter, Thermostat, Fasteners, Plug and socket, Busbars, Spaceheater, busbar, Powersupply, Protection Relay, TCS Relay, Capacitors, Spring Terminals, CTs, Wires, Sheet Steels, Control cables, IP 65, 55 certificates - Found in order
Compliance report email dated on 13.05.2023 - Found in order

## Details of measuring instrument
Sr. No. | Detail of Equipment(s) / Instrument(s) | Range | ID | Validity till Date | Calibration Certificate Number | NABL / OTHER CERT. BODIES / NABL Traceability (type Yes wherever applicable) | NON-NABL (type Yes wherever applicable)
1 | AC HV Divider with Indicator | 0-100kV | BK-2019-07 | 28.06.2023 | TMS/22/01701 Dated: 28.06.2022 | Yes |  | Yes
2 | Digital Insulation Tester | 0-5000VDC | 0357984 | 28.06.2023 | TMS/22/01702 Dated: 28.06.2022 | Yes |  | No
3 | Circuit Breaker Analyzer | 20-150 msec | 3015.00AI0392 | 28.06.2023 | TMS/22/01703 Dated: 28.06.2022 | Yes
4 | Digital Clamp Meter | multi | 20124143 | 28.06.2023 | TMS/22/01704 Dated: 28.06.2022 | Yes
5 | Digital DC Ammeter | 0-150A/7mV | 1228527 | 28.06.2023 | TMS/22/01705 Dated: 28.06.2022 | Yes
6 | Digital DC Mili Voltmeter | 0-200mV | 1502078 | 28.06.2023 | TMS/22/01706 Dated: 28.06.2022 | Yes
7 | DC Current Shunt | 30-150A DC | 020222 | 28.06.2023 | TMS/22/01707 Dated: 28.06.2022 | Yes
8 | Digital 3ph Ammeter | 300A/5A | ACB4200461 | 28.06.2023 | TMS/22/01708 Dated: 28.06.2022 | Yes
9 | Measuring Tape | 0-5000mm | - | 06.07.2023 | CC268822000007078F Dated: 07.07.2022 | Yes
10 | 3KV AC HV Kit | 0-3kV | NTPL/106/22-23 | 15.02.2024 | NTPL/106/22-23 Dated: 15.02.2023 |  | Yes
11 | Torque Wrench | 20-100Nm | IST-2WM 100 | 06.07.2023 | CC268822000007081F Dated: 07.07.2022 | Yes

## Areas of concerns
Areas Of Concern
Mass Flow Meter Order code mentioned in GA " 8X3B3R-BCECCGAOADSAAASDA2+AAEEEJFFJBJCKPZ1 " but in meter mentioned " 8X3B3R-BCECCGAOADSAAASDA2+#FF# "
Refer : MOM/JSW-Sandur/001 Dated: 09.05.2023
BOM details to be updated in line with CRP panel

## Pending Activities
Pending Activities from this visit
NIL

## Conclusion
Note: Data filled in this sheet will not upload in TIIMES
Non Conformities raised / Discrepancies observed during Inspection (If Any, Mention TUV India NCR Number ):
Identification of Inspected Item(s):
Conclusion (Acceptable / Not Acceptable / Acceptance subject to):
IRN can be issued for PO Item numbers:
Expenses:
Remarks: