## Notes
Notes:
Data filled in General and conclusion Sections will not upload in TIIMES. Please use these sections to keep data ready for copy paste.
Data in Item Description columns of Accepted Quantity and cumulative Accepted quantity must be verified thoroughly before uploading in TIIMES.
Pending activity, Areas of concern & Details of measuring instruments sheets are applicable for IVR.
Select options from drop down list for unit of measurement (Item Description) & certifying body of measuring instruments (Details of measuring instruments).
Do not modify this format.
To start next row in cell itself use below shortcut: press 'alt + Enter' keys together. Alt + Enter

## General
Note: - Data filled in this sheet will not upload in TIIMES
Title | Details
Control Number
SAP number
Notification Number
Project Name & Location
Client Name
End User Name
DEC / PMC / EPC Name
DEC / PMC / EPC Number
Vendor Name
PO Number (Client PO on Vendor)
Sub Vendor
PO Number (Vendor PO on Sub Vendor)
Inspection Location
Inspection Date(s)

## Item Description
Po Item No. | Item Code | Item Description | Unit | Po Quantity | Offered Quantity | Accepted Quantity (Please verify thouroghly before using this Column for IRN) | Cumulative Accepted Quanitity (for IRN Only)
10 | 002AS0100143IB | TUBE SMLS , OD-38.1 X 4.0 THK X 12000mm Lg. Mat: SA 213 GR T11 End preparation: PLAIN BOTH ENDS Heat No. 3117999 / 2119603 | meter | 2950 | 228 (19 nos) + 1788 (149 nos) | 228 (19 nos) + 1788 (149 nos) | 228 (19 nos) + 1788 (149 nos) | number
meter
km
meter (number)
km (number)
each
Piece
Test sample
AU - All Unit
lot
Set
Running Meter
kg
metric ton (tonne)
ton
cubic millimetre
cubic centimeter
cubic meter
cubic inch
cubic foot
mm
cm
in
foot
mile
yard
liter
kl
cl
ml
g
lb
oz
Sq. mm
Sq. cm
Sq. meter
Sq. in
Sq. foot

## Reference Documents
Sr. No. | Document Name | Client Document Number | Vendor Document Number | Approval Status
1 | PR/MR/ARM | PTS Nr.: AS-TUBE-IBR-242-19 REV-0 | NA | NA
2 | QAP/ITP/QCP | NA | ITP /2021/TSPL/6714003644 & 6714003645, Rev.0 | Approved by Mr. Sadik Ali
3 | Drawing(s) | NA | NA | NA
4 | Procedure(s) | NA | NA | NA
5 | Datasheet(s) | NA | NA | NA
6 | Others (Specify) | NA | NA | NA

## Stages Witnessed
Stages Witnessed
As per ITP 4.0 : Mechanical test on product sample witnessed one sample per heat /size for (Tensile, flattening, flaring, hardness) - Found to meet the specification requirement.
As per ITP 5.0 : Chemical test on product sample witnessed one sample per heat /size- Found to meet the specification requirement.
As per ITP 6.0 : Hydrostatic test witnessed on 10% randomly selected at 2000 Psi (g) for 5 Seconds holding time from each item - No Leakage nor No Pressure drop observed during holding time
s per ITP 8.0 & 10.0 : Visual checked for surface finish, workmanship, Markings on tubes at randomly selected 10% pipes done after hydrostatisc test – Found free of injurious defects & marking & colour coding found in order.
As per ITP 9.0 : Dimension checked on 10% randomly selected tubes (OD, thickness, length etc)- Found to meet material specification requirements.

## Document reviewed
Document reviewed
As per ITP 1.0 : Raw material Mill MTC checked its content as declared by supplier.- found to meet the specification requirements.
As per ITP 2.0: Heat treatment report reviewed as declared by supplier- Found in order.
As per ITP 7.0: eddy current test report reviewed as declared by supplier- Found in order.
As per ITP 11.0: Internal hydro test, visual inspection & dimensional report reviewed as provided by supplier- Found in order.
As per ITP 11.0: Manufacturer's/Mill test certificate reviewed as provided by supplier- Found in order.

## Details of measuring instrument
Sr. No. | Detail of Equipment(s) / Instrument(s) | Range | ID | Validity till Date | Calibration Certificate Number | NABL / OTHER CERT. BODIES / NABL Traceability (type Yes wherever applicable) | NON-NABL (type Yes wherever applicable)
1 | Micrometer | 0-25mm | NA03/25/01 | 28.02.2022 | JSL-893 DT. 01.09.21 | No |  | Yes
2 | Micrometer | 25-50mm | NA03/50/01 | 30.09.2022 | JSL-901 | No |  | No
3 | Measuring tape | 0-15 mtr | JSL-MT-15 | 01.12.2021 | ME.2021/06/08/001 DT. 02.06.21 | Yes
4 | External micrometer | 300-400mm | M400/20 | 18.02.2022 | 21-31072 DT. 19.2.22 | Yes
5 | Bevel Protector | 0˚-90˚-0˚ | BP-01 | 31.12.2021 | ME.2021/01/08 /001 Dt. 01.01.21 | Yes
6 | Pressure gauge | 0-420 kg/cm2g | PG-420/20 | 29.11.2021 | JSL-420/20 DTD 30.08.2021 | No
7 | Pressure Recorder | 0-30000 Psi | NA03/PIR-01 | 29.12.21 | ET.2021/08/96/065 DT, 30.08.21 | Yes
8 | Universal testing machine | 0-1000 kN | 8/2003-2956 | 16.08.2022 | SME/21/1457 DT. 17.08.2021 | Yes
9 | Pressure gauge | 0-420 kg/cm2g | PG-420/29 | 25.01.2022 | JSL-420/29 DT. 26.10.21 | No

## Areas of concerns
Areas Of Concern
Nil

## Pending Activities
Pending Activities from this visit
Nil

## Conclusion
Note: Data filled in this sheet will not upload in TIIMES
Non Conformities raised / Discrepancies observed during Inspection (If Any, Mention TUV India NCR Number ):
Identification of Inspected Item(s):
Conclusion (Acceptable / Not Acceptable / Acceptance subject to):
IRN can be issued for PO Item numbers:
Expenses:
Remarks: