## Notes
Notes:
Data filled in General and conclusion Sections will not upload in TIIMES. Please use these sections to keep data ready for copy paste.
Data in Item Description columns of Accepted Quantity and cumulative Accepted quantity must be verified thoroughly before uploading in TIIMES.
Pending activity, Areas of concern & Details of measuring instruments sheets are applicable for IVR.
Select options from drop down list for unit of measurement (Item Description) & certifying body of measuring instruments (Details of measuring instruments).
Do not modify this format.
To start next row in cell itself use below shortcut: press 'alt + Enter' keys together. Alt + Enter

## General
Note: - Data filled in this sheet will not upload in TIIMES
Title | Details
Control Number
SAP number
Notification Number
Project Name & Location
Client Name
End User Name
DEC / PMC / EPC Name
DEC / PMC / EPC Number
Vendor Name
PO Number (Client PO on Vendor)
Sub Vendor
PO Number (Vendor PO on Sub Vendor)
Inspection Location
Inspection Date(s)

## Item Description
Po Item No. | Item Code | Item Description | Unit | Po Quantity | Offered Quantity | Accepted Quantity (Please verify thouroghly before using this Column for IRN) | Cumulative Accepted Quanitity (for IRN Only)
1 | N/A | Structural Steel As Per IRN Annexure no- TOYO/SISCOL/IRN/2023-2024/U3-034A Dt- 13.03.2023 (Qty- 48 Nos) | metric ton (tonne) | 2000 | 12.493 | 12.493 | 12.493 | number
2 | N/A | Structural Steel As Per IRN Annexure no- TOYO/SISCOL/IRN/2023-2024/U3-034B Dt- 13.03.2023 (Qty- 60 Nos) | metric ton (tonne) | 2000 | 13.837 | 13.837 | 13.837 | meter
km
meter (number)
km (number)
each
Piece
Test sample
AU - All Unit
lot
Set
Running Meter
kg
metric ton (tonne)
ton
cubic millimetre
cubic centimeter
cubic meter
cubic inch
cubic foot
mm
cm
in
foot
mile
yard
liter
kl
cl
ml
g
lb
oz
Sq. mm
Sq. cm
Sq. meter
Sq. in
Sq. foot

## Reference Documents
Sr. No. | Document Name | Client Document Number | Vendor Document Number | Approval Status
1 | PR/MR/ARM | N/A | N/A | N/A
2 | QAP/ITP/QCP | TY-1P28A-CV-SW001-QCP-0001-02 | SISCOL/TOYO/NRL/QAP/080 Rev-01 Date- 14.09.2022 | Approved By Client
3 | Drawing(s) | As Per Offer List no- (A) TOYO/SISCOL/IRN/2023-2024/U3-034 A Dt- 13.03.2023 (B) TOYO/SISCOL/IRN/2023-2024/U3-034 B Dt- 13.03.2023 | N/A | Approved By Client
4 | Procedure(s) | TP-1ZZZA-CV-SPE-0009 D1, TP-1ZZZA-CV-SPE-0021,TES A-322/PR/PS, TP-1ZZZA-PI-SPE-0003_D3 | N/A | Approved By Client
5 | Datasheet(s) | TY-1P28A-CM-SW001-PRC-00003-A2 | N/A | Approved By Client
6 | Others (Specify) | IS 2062-2011, IS 800, IS 808, IS 7215, IS 9595, ISO 8501, ISO 8502,ISO 2808, ASTM D6677, NACE SP0188 | N/A | Reference document.

## Stages Witnessed
Stages Witnessed
As per QAP Clause No- 5.3 – (a) Random witnessed Visual & Size and DP test of Fillet welds as per QAP/Drawing and found satisfactory. (b) Random witness for Ultrasonic test as per applicable member and QAP specification and found no relevant indication.
As per QAP Clause No- 6.1- Random Final Dimension and Visual Inspection performed for offered Items as per QAP/Drawing/Project Specification and found acceptable.
As per QAP Clause No- 7.2 for final paint inspection-Witnessed 100 % Final Painting DFT checked found within acceptable limit and Color shade verified found as per specification.
As per QAP Clause No- 7.2 for final paint inspection- Holiday testing conducted on 10 % randomly selected sample in accordance with NACE SP0188 by wet sponge pinhole detector at 90 V, found acceptable.
As per QAP Clause No- 7.2 - For Witnessed Finish paint DFT on Test Panel as per QAP/Painting Specification and found meet the requirements and Adhesion test will be carried out after one week.

## Document reviewed
Document reviewed
As per QAP clause No: 1.1 Reviewed QAP, WPS/PQR/WPQ, NDE Procedure & Painting Procedures as per Project Specification & relevant codes and found in order.
As per QAP clause No : 2.1 – Reviewed Material Test certificates for Plates, Hot rolled sections for Correlation of Heat No/Batch No and found in order.
As per QAP Clause No- 2.2- Reviewed Internal Inspection Report for Visual & dimension of Materials as per QAP & Specification and found in order.
As per QAP Clause No- 3.2- Reviewed Batch Test reports of Painting Materials as per QAP/Painting Specification and found in order.
As per QAP Clause No- 3.3- Reviewed Batch Test Certificates of welding consumables as per QAP/ASME Sec II Part C and found in order.
As per QAP Clause No- 4.1- Reviewed WPS/PQR/WQT as per ASME Sec IX and found in order.
As per QAP Clause No- 5.1- Reviewed Stage inspection report for Cutting of Plates/Rolled Sections as per Drawing and found in order.
As per QAP Clause No- 5.2- Reviewed Fit-up reports for offered Items as per Drawing and found in order.
As per QAP Clause No- 7.1- Surface Cleaning & Preparation reports for cellophane tape test, salt contamination, blast profile measurement for offered Items as per QAP/Painting Specification and found in order.
Verified Calibration status of Testing Equipment/Measuring Instruments and found Valid

## Details of measuring instrument
Sr. No. | Detail of Equipment(s) / Instrument(s) | Range | ID | Validity till Date | Calibration Certificate Number | NABL / OTHER CERT. BODIES / NABL Traceability (type Yes wherever applicable) | NON-NABL (type Yes wherever applicable)
Yes
No

## Areas of concerns
Areas Of Concern

## Pending Activities
Pending Activities from this visit

## Conclusion
Note: Data filled in this sheet will not upload in TIIMES
Non Conformities raised / Discrepancies observed during Inspection (If Any, Mention TUV India NCR Number ):
Identification of Inspected Item(s):
Conclusion (Acceptable / Not Acceptable / Acceptance subject to):
IRN can be issued for PO Item numbers:
Expenses:
Remarks: