## Notes
Notes:
Data filled in General and conclusion Sections will not upload in TIIMES. Please use these sections to keep data ready for copy paste.
Data in Item Description columns of Accepted Quantity and cumulative Accepted quantity must be verified thoroughly before uploading in TIIMES.
Pending activity, Areas of concern & Details of measuring instruments sheets are applicable for IVR.
Select options from drop down list for unit of measurement (Item Description) & certifying body of measuring instruments (Details of measuring instruments).
Do not modify this format.
To start next row in cell itself use below shortcut: press 'alt + Enter' keys together. Alt + Enter

## General
Note: - Data filled in this sheet will not upload in TIIMES
Title | Details
Control Number
SAP number
Notification Number
Project Name & Location
Client Name
End User Name
DEC / PMC / EPC Name
DEC / PMC / EPC Number
Vendor Name
PO Number (Client PO on Vendor)
Sub Vendor
PO Number (Vendor PO on Sub Vendor)
Inspection Location
Inspection Date(s)

## Item Description
Po Item No. | Item Code | Item Description | Unit | Po Quantity | Offered Quantity | Accepted Quantity (Please verify thouroghly before using this Column for IRN) | Cumulative Accepted Quanitity (for IRN Only)
10 | CAPEQP105213 | CRUDE CONDENSER CS 5.4 M2,TAG NO : E-111 | each | 1 | 1 | 1 | 1 | number
20 | CAPEQP105214 | CRUDE CONDENSER CS 13.8 M2,TAG NO : E-113, AS PER DRAWING CRUDE CONDENSER-1 | each | 1 | 1 | 1 | 1 | meter
30 | CAPEQP105215 | CHILLED WATER COOLER CS,8.1M2 ,TAG NO : E-117 | each | 1 | 1 | 1 | 1 | km
40 | CAPEQP105216 | LE COL CONDENSER CS ,18.7 M2, TAG NO : E-122 | each | 1 | 1 | 1 | 1 | meter (number)
50 | CAPEQP105217 | LE COL SEC.CONDENSER LTCS ,2.4 M2, TAG NO : E-123 | each | 1 | 1 | 1 | 1 | km (number)
60 | CAPEQP105218 | PDT COL.CONDENSER CS,24.7 M2,TAG NO : E-125 | each | 1 | 1 | 1 | 1 | each
70 | CAPEQP105219 | PRODUCT COOLER CS , 4 M2 ,TAG NO : E-127 | each | 1 | 1 | 1 | 1 | Piece
80 | CAPEQP105220 | COMPRESSOR FEED COOLER ,CS ,6.1 M2 , TAG NO : E-129 | each | 1 | 1 | 1 | 1 | Test sample
90 | CAPEQP105221 | MDC VAPOURIZER, SS 316L 7.9 M2 ,TAG NO : E-132 AS PER DRAWING R1 VAPORIZER | each | 1 | 1 | 1 | 1 | AU - All Unit
100 | CAPEQP105222 | MDC SUPERHEATER SS 316L,5.9 M2, TAG NO : E-133 AS PER DRAWING R1 SUPERHEATER | each | 1 | 1 | 1 | 1 | lot
110 | CAPEQP105223 | HCL COL FEED COOLER SS 316L,18.5 M2,TAG NO : E-137 | each | 1 | 1 | 1 | 1 | Set
120 | CAPEQP171284 | SHELL & TUBE CONDENSER, SA 106 GR B ,1.9 M2 TAG NO : E-124,LE COL.REBOILER | each | 1 | 1 | 1 | 1 | Running Meter
130 | CAPEQP171285 | SHELL & TUBE CONDENSER SA 106 GR B ,6.1 M2 TAG NO : E-138,RMI FEED COOLER | each | 1 | 1 | 1 | 1 | kg
140 | CAPEQP171286 | SHELL & TUBE CONDENSER SA 106 GR B ,2.3 M2 TAG NO : E-140,RMI DAY TANK CIRCULATION COOLER | each | 1 | 1 | 1 | 1 | metric ton (tonne)
150 | CAPEQP171287 | SHELL & TUBE CONDENSER, SA 106 GR B ,4.3 M2 TAG NO :E-141A/B, RM1 STORAGE VENT CONDENSER | each | 2 | 2 | 2 | 2 | ton
cubic millimetre
cubic centimeter
cubic meter
cubic inch
cubic foot
mm
cm
in
foot
mile
yard
liter
kl
cl
ml
g
lb
oz
Sq. mm
Sq. cm
Sq. meter
Sq. in
Sq. foot

## Reference Documents
Sr. No. | Document Name | Client Document Number | Vendor Document Number | Approval Status
1 | PR/MR/ARM | Not Applicable | Not Applicable | Not Applicable
2 | QAP/ITP/QCP | Not Applicable | QAP/22-23/NFIL/02 REV-01 | Approved by Customer vide email dated : 16.11.2022
3 | Drawing(s) | Not Applicable | DRGWO1922-64-NFIL SHEET 1 OF 1 REV-03(E -111), DRGWO2223-68-NFIL SHEET 1 OF 1 REV-02(E -113 ), DRGWO2223-67-NFIL SHEET 1 OF 1 REV-02(E -117 ), DRGWO2223-62-NFIL SHEET 1 OF 1 REV-03(E -122 ), DRGWO2223-58-NFIL SHEET 1 OF 1 REV-03(E -123 ), DRGWO2223-57-NFIL SHEET 1 OF 1 REV-04 (E-125), DRGWO2223-63-NFIL SHEET 1 OF 1 REV-03 (E-127), DRGWO2223-66-NFIL SHEET 1 OF 1 REV-03 (E-129), DRGWO1922-71-NFIL SHEET 1 OF 1 REV-03(E -132), DRGWO2223-65-NFIL SHEET 1 OF 1 REV-03(E -133), NFIL-ARGO-PI-NOD-16 REV-0 ( REFERENCE DRAWING ISSUED BY CLIENT FOR TAG NO : E-133) DRGWO2223-70-NFIL SHEET 1 OF 1 REV-02(E -137), DRGWO2223-69-NFIL SHEET 1 OF 1 REV-02(E -124 ), DRGWO2223-59-NFIL SHEET 1 OF 1 REV-03(E -138 ), DRGWO2223-60-NFIL SHEET 1 OF 1 REV-03 (E-140), DRGWO2223-61-NFIL SHEET 1 OF 1 REV-01(E -141A/B), | E-111 Drawing Approved vide email dated : 27.12.2022, E-113,Drawing Approved vide email dated : 31.12.2022, E-117,E-137 Drawing Approved vide email dated : 14.12.2022, E-122 & E-125 Drawing Approved vide email dated : 27.12.2022, E-123,E-127,E-129,E-132,E-138,E-140 Drawing Approved vide email dated :09.12.2022, E-133 Drawing Approved vide email dated : 10.01.2023, E-124 Drawing Approved vide email dated : 03.12.2022, E-141A/B Drawing Approved vide email dated : 15.12.2022
4 | Procedure(s) | Not Applicable | Not Applicable | Not Applicable
5 | Datasheet(s) | Not Applicable | Not Applicable | Not Applicable
6 | Others (Specify) | Not Applicable | Not Applicable | Not Applicable

## Stages Witnessed
Stages Witnessed
As per QAP Clause : 1,2, ( Materials ), Witnessed Material identification of Pressure parts ( Plates , Pipes , Nozzle Flanges , Girth flanges , Tube sheets ) at Vendor location - Found complying to drawing requirements except some change in MOC is accepted by client .
As per QAP Clause :3, ( Materials ), Witnessed Material identification of Tubes ( at random ) at Sub-Vendor location - Found complying to drawing requirements.
As per QAP Clause : 15 ( Final inspection before hydro test) , Witnessed Final visual & dimensional inspection after all fabrication activity - Visual on accessible locations - Found free from defects,Dimensional inspection on accessible parts - Found complying to drawing requirements except some deviations is accepted by client .
As per QAP Clause : 16 ( Pressure testing ) , Witnessed Final hydro test of shell side & Tube side , Test pressures as per approved drawing for each Equipment in horizontal condition for a minimum holding period of one hour- No visible leakages nor pressure drop observed during holding period , Verified pressure gauge ID & Validity during testing & Found satisfactory.

## Document reviewed
Document reviewed
As per QAP Clause : 1,2,3 ( Materials ) , Reviewed Material History chart along with material test certificates for Pressure parts ( Plates , Pipes , Flanges , girth flanges , tube sheets & tubes ) - Found complying to drawing requirements except some deviations in MOC accepted by client .
As per QAP Clause : 1 ( In process inspection ) , Reviewed Long seam set up inspection records as declared by vendor - Found complying to drawing requirements except some deviations in Length accepted by client .
As per QAP Clause : 2 ( In process inspection ) , Reviewed Back chip DP reports for Long seams (as applicable) as declared by vendor - Found in order .
As per QAP Clause : 3 ( In process inspection ) , Reviewed Shell to shell Cir-seam set up inspection records ( as applicable ) as declared by vendor - Found complying to drawing requirements except some deviations in Length accepted by client .
As per QAP Clause : : 4 ( In process inspection ) , Reviewed Back chip DP reports for Cir-seams ( as applicable ) as declared by vendor - Found in order .
As per QAP Clause : 5 ( In process inspection ) , Interpretation of RT Films as applicable as per drawing , Reviewed RT Summart chart & verified with RT reports -Found complying to drawing requirements .
As per QAP Clause : 6 ( In process inspection),Reviewed Dish end inspection records as declared by vendor -Found complying to drawing requirements
As per QAP Clause : 7 ( In process inspection),Reviewed Tube sheet inspecction records as declared by vendor after machining & drilling - Found complying to drawing requirements
As per QAP Clause : 8( In process inspection),Reviewed Channel to Dish end / Girth flange set up reports as declared by vendor - Found complying to drawing requirements
As per QAP Clause : 9 ( In process inspection ) , Reviewed Back chip DP reports for Channel shell to Dish Cirseam as declared by vendor - Found in order .
As per QAP Clause : 10 ( In process inspection ) , Reviewed Nozzle to Exchanger set up reports as declared by vendor - Found complying to drawing requirements except some deviations accepted by client .
As per QAP Clause : 11 ( In process inspection ) , Reviewed Back chip DP reports for nozzle to excanger as declared by vendor - Found in order .
As per QAP Clause : 12( In process inspection ) , Reviewed Nozzle RF pad Pneumatic test reports as declared by vendor ( as applicable ) -Found complying to ITP requirements
As per QAP Clause : 13( In process inspection ) , Reviewed Tube bundle Skelton inspection records as declared by vendor - Found complying to drawing requirements
As per QAP Clause : 14 ( In process inspection ) , Reviewed tube sheet to shell set up reports as declared by vendor - Found complying to drawing requirements
As per QAP Clause : 15,16 ( Final inspection before painting ), Reviewed witness inspection records for final visual & dimensions , Pressure testing - Found complying to drawing requirements except some dimensional deviations accepted by client
As per QAP Clause : 17 , Reviewed Painting reports for CS exchangers , Pickling & passivation for SS exchangers - Found in order.
As per QAP Clause : 18 ( Final inspection after painting ) , Reviewed vendor report for completeness of all requirements , Finish , Name plate attachment - Found in order .

## Details of measuring instrument
Sr. No. | Detail of Equipment(s) / Instrument(s) | Range | ID | Validity till Date | Calibration Certificate Number | NABL / OTHER CERT. BODIES / NABL Traceability (type Yes wherever applicable) | NON-NABL (type Yes wherever applicable)
Yes
No

## Areas of concerns
Areas Of Concern

## Pending Activities
Pending Activities from this visit

## Conclusion
Note: Data filled in this sheet will not upload in TIIMES
Non Conformities raised / Discrepancies observed during Inspection (If Any, Mention TUV India NCR Number ):
Identification of Inspected Item(s):
Conclusion (Acceptable / Not Acceptable / Acceptance subject to):
IRN can be issued for PO Item numbers:
Expenses:
Remarks: