## Notes
Notes:
Data filled in General and conclusion Sections will not upload in TIIMES. Please use these sections to keep data ready for copy paste.
Data in Item Description columns of Accepted Quantity and cumulative Accepted quantity must be verified thoroughly before uploading in TIIMES.
Pending activity, Areas of concern & Details of measuring instruments sheets are applicable for IVR.
Select options from drop down list for unit of measurement (Item Description) & certifying body of measuring instruments (Details of measuring instruments).
Do not modify this format.
To start next row in cell itself use below shortcut: press 'alt + Enter' keys together. Alt + Enter

## General
Note: - Data filled in this sheet will not upload in TIIMES
Title | Details
Control Number
SAP number
Notification Number
Project Name & Location
Client Name
End User Name
DEC / PMC / EPC Name
DEC / PMC / EPC Number
Vendor Name
PO Number (Client PO on Vendor)
Sub Vendor
PO Number (Vendor PO on Sub Vendor)
Inspection Location
Inspection Date(s)

## Item Description
Po Item No. | Item Code | Item Description | Unit | Po Quantity | Offered Quantity | Accepted Quantity (Please verify thouroghly before using this Column for IRN) | Cumulative Accepted Quanitity (for IRN Only)
00010 | 1300041192 | Carbon Steel Cold Drawn Seamless annealing & fully killed U-bend tubes conforming to the Specification as per ASME SA 210 Gr. A1 of ASME SEC. II Part-A, Ed. 2021. Size: 19.00mm OD X 2.11mm THK (Min.) X 3000mm Leg Length. | number | 84 Nos. | 84 Nos. | 84 Nos. | 84 Nos. | number
meter
km
meter (number)
km (number)
each
Piece
Test sample
AU - All Unit
lot
Set
Running Meter
kg
metric ton (tonne)
ton
cubic millimetre
cubic centimeter
cubic meter
cubic inch
cubic foot
mm
cm
in
foot
mile
yard
liter
kl
cl
ml
g
lb
oz
Sq. mm
Sq. cm
Sq. meter
Sq. in
Sq. foot

## Reference Documents
Sr. No. | Document Name | Client Document Number | Vendor Document Number | Approval Status
1 | PR/MR/ARM | Not Applicable | Not Applicable | Not Applicable
2 | QAP/ITP/QCP | Not Applicable | STPL/QAP/1371/22-23, REV.00, Dated: 03.06.2022 | Approved By MRPL
3 | Drawing(s) | D-420-00501A | Not Applicable | Provided By MRPL
4 | Procedure(s) | Not Applicable | Not Applicable | Not Applicable
5 | Datasheet(s) | Not Applicable | Not Applicable | Not Applicable
6 | Others (Specify) | [1] EA 2009/42009, Rev.0. [2] ONGC SPEC.: 00-ES-400-005, Rev.01. Dt. 30.11.2010. | Not Applicable | Provided By MRPL & ONGC.

## Stages Witnessed
Stages Witnessed
As per QAP stage no- 3: Sampling carried out for Chemical test [Product analysis] & Mechanical test as Tensile, Hardness, Flaring and Flattening as per approved ITP and relevant standard - found satisfactory
As per QAP stage no- 4: Witnessed Mechanical tests (Tensile, Flattening, Flaring and Hardness Test) at manufacture in house testing Lab facilities - results found to meet the specification requirements
As per QAP stage no-.8: Witnessed hydrostatic test at testing pressure 1000 PSI [G] for 10% Qty randomly selected Quantity of U tubes in final length as per approved QAP- No Leakage / No Pressure drop observed during 120 seconds ( Min. ) holding time., hence test found satisfactory.
As per QAP stage no-.9: Visual inspection carried out at Internal & external surface as accessible area for surface finish on10% Qty randomly selected Quantity of U tubes in final length as per approved QAP – No injurious surface defects & Nor mechanical damages were observed, Hence Found satisfactory.
As per QAP stage no-. 9: Dimension checked on 10% random selected quantity of U tubes in final length from offer lot as per approved QAP– observed dimension found within tolerance limits as per standard requirements.
As per QAP stage no- 9: Verified Product Marking on U tubes in final length as per approved QAP– found satisfactory.
All measuring instruments/ equipment were verified for continued suitability for intended use, proper identification, calibration status, traceability to national standards & found satisfactory.

## Document reviewed
Document reviewed
As per QAP stage No. 1: Reviewed Photocopy of Raw material test certificates as declared by vendor as per approved ITP - Found to meet the specification requirements
As per QAP stage No. 2 : Reviewed Heat treatment (Annealing condition) chart / record as per approved QAP - Found in order.
As per QAP stage No- 5. : Reviewed Chemical analysis (Product analysis) test report as per approved QAP - mentioned chemical elements found to meet the relevant standard requirements.
As per QAP stage No- 6: Reviewed Mock up test report [inner most two row] as per approved QAP - Found Satisfactory.
As per QAP stage No- 7. : Reviewed U bend portion + 300 MM chart as per approved QAP - Found Satisfactory.
Reviewed calibration certificates of measuring instruments and pressure gauges - Found in order to have valid calibration for intended use.
As per QAP stage No. 10 : Reviewed of manufacture final test certificate [ EN 10204 Typ. 3.2] TC No. 1371/22-23, Dtd. 31.07.2022 - Found in order.

## Details of measuring instrument
Sr. No. | Detail of Equipment(s) / Instrument(s) | Range | ID | Validity till Date | Calibration Certificate Number | NABL / OTHER CERT. BODIES / NABL Traceability (type Yes wherever applicable) | NON-NABL (type Yes wherever applicable)
1 | Flat micrometer [OD] | 0-25mm | 67497917 | 13.08.2022 | EX/M/2021/08/34 | Yes | Yes | Yes
2 | Ball point micrometer [THK.] | 0-25mm | 36205207 | 25.02.2023 | EX/M/2022/02/77 | Yes | No | No
3 | Measuring Tape | 0-15 Mtrs. | MT-01 | 15.08.2022 | 21-MHC-16-13-001 | Yes | No
4 | Pressure Gauge | 0-210 KK/CM2 [G] | MPC211813J | 14.09.2022 | NCQC-M/150921/38 | Yes | No

## Areas of concerns
Areas Of Concern
During inspection Photography strictly prohibited at M/s. Sainest Tubes Private Limited.

## Pending Activities
Pending Activities from this visit
None.

## Conclusion
Note: Data filled in this sheet will not upload in TIIMES
Non Conformities raised / Discrepancies observed during Inspection (If Any, Mention TUV India NCR Number ):
Identification of Inspected Item(s):
Conclusion (Acceptable / Not Acceptable / Acceptance subject to):
IRN can be issued for PO Item numbers:
Expenses:
Remarks: