## Notes
Notes:
Data filled in General and conclusion Sections will not upload in TIIMES. Please use these sections to keep data ready for copy paste.
Data in Item Description columns of Accepted Quantity and cumulative Accepted quantity must be verified thoroughly before uploading in TIIMES.
Pending activity, Areas of concern & Details of measuring instruments sheets are applicable for IVR.
Select options from drop down list for unit of measurement (Item Description) & certifying body of measuring instruments (Details of measuring instruments).
Do not modify this format.
To start next row in cell itself use below shortcut: press 'alt + Enter' keys together. Alt + Enter

## General
Note: - Data filled in this sheet will not upload in TIIMES
Title | Details
Control Number
SAP number
Notification Number
Project Name & Location
Client Name
End User Name
DEC / PMC / EPC Name
DEC / PMC / EPC Number
Vendor Name
PO Number (Client PO on Vendor)
Sub Vendor
PO Number (Vendor PO on Sub Vendor)
Inspection Location
Inspection Date(s)

## Item Description
Po Item No. | Item Code | Item Description | Unit | Po Quantity | Offered Quantity | Accepted Quantity (Please verify thouroghly before using this Column for IRN) | Cumulative Accepted Quanitity (for IRN Only)
1 |  | Supply of Water Seal Relief Tank ,F­379 As Per PO : 40325 | each | 1 | 1 | 1 | 1 | number
meter
km
meter (number)
km (number)
each
Piece
Test sample
AU - All Unit
lot
Set
Running Meter
kg
metric ton (tonne)
ton
cubic millimetre
cubic centimeter
cubic meter
cubic inch
cubic foot
mm
cm
in
foot
mile
yard
liter
kl
cl
ml
g
lb
oz
Sq. mm
Sq. cm
Sq. meter
Sq. in
Sq. foot

## Reference Documents
Sr. No. | Document Name | Client Document Number | Vendor Document Number | Approval Status
1 | PR/MR/ARM | MT-P20P02-D1PPT-MBC002-LTH-P-00 | Not Applicable | RIL Document
2 | QAP/ITP/QCP | P26005-MT-P20P02-D1PPT-MBC002-LTH-P-00-A-PT401-A05-0006-03 | SSIS/21/QCP/U/19 REV-03 | Approved in Code-1 by RIL & LTHE ( Work may proceed)
3 | Drawing(s) | P26005-MT-P20P02-D1PPT-MBC002-LTH-P-00-A-PT401--B02-0006-06 | 20049-MEC-DRG-2008 REV-06 | Approved in Code-1 by RIL & LTHE ( Work may proceed)
4 | Procedure(s) | P26005-MT-P20P02-D1PPT-MBC002-LTH-P-00-A-PT401-J04-0077-00 ( Pickling & passivation procedure ) P26005-MT-P20P02-D1PPT-MBC002-LTH-P-00-A-PT401-J04-0078-01 ( Surface preparation & painting procedure ), P26005-MT-P20P02-D1PPT-MBC002-LTH-P-00-A-PT401-J01-0077-01 (Weld Procedures ) , P26005-MT-P20P02-D1PPT-MBC002-LTH-P-00-A-PT401-M02-0077-01 ( Preservation , Packing & Shipping procedure ), P26005-MT-P20P02-D1PPT-MBC002-LTH-P-00-A-PT401-J02-0077-01 (NDE Procedure ), P26005-MT-P20P02-D1PPT-MBC002-LTH-P-00-A-PT401-K02-0077-01 ( Leak Test Procedure ), P26005-MT-P20P02-D1PPT-MBC002-LTH-P-00-A-PT401-K07-0077-01 ( PMI ) | 20049-QC-DOC-1281 Rev-00( Pickling & passivation procedure ), 20049-QC-DOC-1261 Rev-01 ( Surface preparation & painting procedure ), SSIS/21/WM/01 Rev-01 ( Weld Procedures), 20049-QC-DOC-1263 Rev-00 ( Preservation , Packing & Shipping procedure ), SS-NDE-01 REV-00 ( NDE Procedures ), 20049-QC-DOC-1262 Rev-01 ( Leak test Procedure ), SS-QP-011 Rev-04 ( PMI ) | Approved in Code-1 by RIL & LTHE ( Work may proceed)
5 | Datasheet(s) | Not Applicable | Not Applicable | Not Applicable
6 | Others (Specify) | Not Applicable | Not Applicable | Not Applicable

## Stages Witnessed
Stages Witnessed
As per ITP Clause : 2.1,2.2, Witnessed material identification of plates, Fittings,Flanges , Fasteners, Gaskets & Load bearing parts after receipt at vendor location , Sample identification for plates & its testing at NABL approved Lab ( for Plates with Original MTC not available ).
As per ITP Clause : 2.3, Witness of welding consumables, batch number verification
As per ITP Clause : 3.1, Witnessed Long seam set up of shell courses at random- Found as per drawing /ITP requirements.
As per ITP Clause : 3.2 , Witnessed Visual & dimensional inspection of Top Cone after forming & welding , Verified hardness below 235 BHN for Cone base metals & welds after forming & welding
As per ITP Clause : 3.3, Witnessed Cir- seam set up at random - Found as per drawing /ITP requirements.
As per ITP Clause : 3.6,Witnessed Nozzle set up to vessel at random - Found as per Drawing requirements.
As per ITP Clause : 3.8, Witness of nozzles N1,N6 & N7 ( complete assembly ) set up with shell - Found complying to drawing requirements.
As per ITP Clause : 3.13, a)Witnessed Visual inspection of all welds - No injurious weld defects observed. B) Witnessed Final weld DPT of all butt & fillet welds including load bearing welds from inside & outside, PT of butt welds in plate flanges after machining. c) Witnessed PT on temporary attachment removed areas , Arc strike removed areas d) Witnessed internal inspection of shell for weld finish , circularity & completeness of assembly. e) Witnessed UT on bottom plate long seams , Fouling weld areas of piping spool cleat pads- No recordable indications observed.
As per ITP Clause : 5.1,Witnessed Pneumatic test of nozzle RF pads @ 1.5Kg/cm2g- No leakage observed from inside & outside of welds .
As per ITP Clause : 5.2 , Witnessed Final Visual inspection of Vessel & piping spools after all fabrication activity - No injurious surface & weld defects observed .
As per ITP Clause : 5.2 , Witnessed Final dimensional inspection of vessel & piping spools after all fabrication activity - Found as per drawing requiements except some deviations observed were accepted by client,.Witnessed assembly of piping spool to vessel- Found as per drawing requirements
As per ITP Clause : 5.3,Wittnessed PMI inspection ( carbon check by OES Method ) for all accessible welds , base metals for vessel after all fabrication activity - Main alloying elements found complying to specification / drawing requirements.
As per ITP Clause : 5.3a, Witnessed Ferrite test of welds ( outside & accessible inside welds ) - Ferrite value observed in range of 3-10 FN - Acceptable.
As per ITP Clause : 6.1 , Witnessed water fill test of vessel after 24 Hours observation by vendor & 6 hours observation done by TPIA - No leakage / bulging of vessel observed - Acceptable.
As per ITP Clause : 6.2 , Witnessed draining & drying of vessel after hydro test & pickling & passivation - No traces of water observed .
As per ITP Clause : 6.3 & 6.4, Witnessed Name plate attachment to vessel , Verified name plate details & name plate hard stamped for identification.
As per ITP Clause : 7 , Witnessed Visual inspection of internal surfaces after pickling & passivation, CuS04 test , Litmus paper test - Found complying to procedure requirements.
As per ITP Clause : 8.1 , Witnessed Visual inspection of externals surfaces , Surface profile check, Salt Contamination test, Humidity , Dew point check after surface preparation at random-Found complying to procedure / ITP requirements.
As per ITP Clause : 8.2,Witnessed visual inspection of paint after each coating , Paint DFT check at random for each coat, MEK test for Type-1 paint, Weather condition check -Found complying to procedure / ITP requirements.
As per ITP Clause : 8.3 , Witnessed Final outside visual , DFT check at random locations , pull out test , adhesion test, Ral shade verifiation - Found complying to procedure / drawing requirements.
As per ITP Clause : 9.1 , Witnessed packing of all nozzles opening except applicable blind flanges , Preservation of vessel inside with silica gel- Found complying to ITP requirements.
As per ITP Clause : 9.2, Witnessed Vessel packing with rapping roll & tarpoline - Found complying to ITP requirements.
As per ITP Clause : 9.3, Witnessed Spare packing , spare verification - Found complying to ITP requirements.
As per ITP Clause : 11, Witnessed vessel marking inspection - Found complying to ITP requirements.

## Document reviewed
Document reviewed
As per ITP Clause : 1.1 , Verified approval of ITP from client.
As per ITP Clause : 1.2,Verified Approval of design calculations , drawings from client .
As per ITP Clause : 1.3, Reviewed WPS / PQR/ WPQ documents - Found complying to drawing / ITP requirements.
As per ITP Clause : 1.4, Reviewed procedures ( NDT,PMI,Pickling & passivation, Surface preparation & painting, water fill test & pneumatic test , Packing & preservation procedure ) & verified approval from client
As per ITP Clause : 2.1 ,2.2 ,2.3,2.4 Reviewed material identification report along with Material test certificates for plates, fittings , flanges,pipes, fasteners & gaskets, NABL Lab test records for plates & pipes, welding consumable MTC along with Test records for IGC PR E test for consumables, Non pressure part MTC - Found complying to specification , drawing & ITP requirements.
As per ITP Clause : 3.2 , Reviewed reports for bottom covers as declared by vendor - Found complying to Drawing requirements.
As per ITP Clause : 3.4 , Reviewed Pipe to flange set up reports as declared by vendor - Found complying to Drawing requirements.
As per ITP Clause : 3.5, Reviewed Fabricated nozzle flange long seam set up reports as declared by vendor-Found complying to Drawing requirements.
As per ITP Clause : 3.6, Reviewed Root Run DP reports as declared by vendor for nozzle to vessel Joints - Found in order.
As per ITP Clause : 3.7, Reviewed back chip DP reports as declared by vendor for applicable seams - Found in order.
As per ITP Clause : 3.9,3.10,3.11,3.12, Reviewed Set up reports for stiffner to nozzles for NPS 2" & Below, Lifting lug pad with Lifting lug to shell,Lifting trunion set up Found complying to Drawing requirements.Reviewed UT reports for areas beneath the lifting lug / trunion pad & for pads .Reviewed set up reports for all internal & external attachments.
As per ITP Clause : 3.13, Reviewed RT films along with RT reports for bottom plate long seams , annular plate long seams , Plate flange long seams, RT Summary chart - Found complying to requirements
As per ITP Clause : 5.3, Reviewed PMI report ( Carbon check by OES Method ) for Piping spools - Found complying to drawing / specification requirements.
As per ITP Clause : 5.4 , Reviewed DP reports for PMI Arc spot removed areas - Found in order.
As per ITP Clause : 6.1, Reviewed Water fill test report for piping spools witnessed by RIL TPIA - Found complying to procedure /ITP requirements.
As per ITP Clause : 8.0, Reviewed Final surface preparation & painting report from NACE qualified inspector along with paint TC - Found complying to procedure /ITP requirements
As per ITP Clause : 10 , Verified compliance to all stages as per ITP ( WPS /PQR/MTC , Stage wise inspection records, Final inspection reports , NDE reports ( RT,UT & DP reports ), Water fill test reports, painting reports ) - Found complying to drawing / ITP / Procedure requirements.
Noted client confirmation email dated : 27.09.2022 from RIL,LTHE, CECO

## Details of measuring instrument
Sr. No. | Detail of Equipment(s) / Instrument(s) | Range | ID | Validity till Date | Calibration Certificate Number | NABL / OTHER CERT. BODIES / NABL Traceability (type Yes wherever applicable) | NON-NABL (type Yes wherever applicable)
Yes
No

## Areas of concerns
Areas Of Concern

## Pending Activities
Pending Activities from this visit

## Conclusion
Note: Data filled in this sheet will not upload in TIIMES
Non Conformities raised / Discrepancies observed during Inspection (If Any, Mention TUV India NCR Number ):
Identification of Inspected Item(s):
Conclusion (Acceptable / Not Acceptable / Acceptance subject to):
IRN can be issued for PO Item numbers:
Expenses:
Remarks: