## Notes
Notes:
Data filled in General and conclusion Sections will not upload in TIIMES. Please use these sections to keep data ready for copy paste.
Data in Item Description columns of Accepted Quantity and cumulative Accepted quantity must be verified thoroughly before uploading in TIIMES.
Pending activity, Areas of concern & Details of measuring instruments sheets are applicable for IVR.
Select options from drop down list for unit of measurement (Item Description) & certifying body of measuring instruments (Details of measuring instruments).
Do not modify this format.
To start next row in cell itself use below shortcut: press 'alt + Enter' keys together. Alt + Enter

## General
Note: - Data filled in this sheet will not upload in TIIMES
Title | Details
Control Number
SAP number
Notification Number
Project Name & Location
Client Name
End User Name
DEC / PMC / EPC Name
DEC / PMC / EPC Number
Vendor Name
PO Number (Client PO on Vendor)
Sub Vendor
PO Number (Vendor PO on Sub Vendor)
Inspection Location
Inspection Date(s)

## Item Description
Po Item No. | Item Code | Item Description | Unit | Po Quantity | Offered Quantity | Accepted Quantity (Please verify thouroghly before using this Column for IRN) | Cumulative Accepted Quanitity (for IRN Only)
10 | CH000073546 | Ball Valve FB WCB SS316 IC ANSI ANSI 150 PFA Lever 100 NB Valve Sr. No. 3V226-1197 to 3V229-1198 Witnessed Valve Sr. No. 3V229-1198 | number | 2 | 2 | 2 | 2 | number
20 | CH000091659 | Ball Valve RB WCB SS316 IC ANSI ANSI 150 PFA Lever 100 NB Valve Sr. No. 3V229-1351 to 3V229-1355, 3V2210- 1173 to 3V2210- 1176, 3V2210-1455 Witnessed Valve Sr. No. 3V2210-1174 | number | 10 | 10 | 10 | 10 | meter
30 | CH000091664 | Ball Valve RB WCB SS316 IC ANSI ANSI 150 PFA Lever 50 NB Valve Sr. No. 3V229-1801 to 3V229-1807 & 3V2210-1410 Witnessed Valve Sr. No. 3V229-1804 | number | 8 | 8 | 8 | 8 | km
meter (number)
km (number)
each
Piece
Test sample
AU - All Unit
lot
Set
Running Meter
kg
metric ton (tonne)
ton
cubic millimetre
cubic centimeter
cubic meter
cubic inch
cubic foot
mm
cm
in
foot
mile
yard
liter
kl
cl
ml
g
lb
oz
Sq. mm
Sq. cm
Sq. meter
Sq. in
Sq. foot

## Reference Documents
Sr. No. | Document Name | Client Document Number | Vendor Document Number | Approval Status
1 | PR/MR/ARM | Not applicable | Not applicable | Not applicable
2 | QAP/ITP/QCP | Not applicable | QAP_PO_4550383322_BV Rev-00 | Approved by Aarti industries through Mail
3 | Drawing(s) | Not applicable | GA-CS-PFAL-RB-BV-LO-AARTI-03032022-02 REV-R1, GA-CS-PFAL-FB-BV-LO-AARTI-03032022-01 REV-R1 | Approved by Aarti industries through Mail
4 | Procedure(s) | Not applicable | Not applicable | Not applicable
5 | Datasheet(s) | Not applicable | Not applicable | Not applicable
6 | Others (Specify) | Not applicable | Not applicable | Not applicable

## Stages Witnessed
Stages Witnessed
QAP Sr. No. 4 & 5 Dimensional checked including end flanges dimensions on 10% randomly selected offered Items as per approved Drawing – Found to meet the approved drawing and dimensional standard requirement.
QAP Sr. No. 6 Witnessed Spark Test at 15 KV DC on 10% randomly selected qty as per approved drawing and approved QAP - Found in order.
QAP Sr. No. 7 & 8 Witnessed Hydrostatic Leakage Shell & Seat test after lining for offered Items on 10% randomly selected qty as per approved drawing and purchase order requirements - No Leakage / No Pressure drop observed during holding time.
QAP Sr. No. 9 Witnessed Pneumatic Seat test for offered Items on 10% randomly selected qty as per approved drawing and purchase order requirements - No Leakage / No Pressure drop observed during holding time.
Visual inspection carried out for Offered Items on 10% qty for surface finish & defects - No injurious surface defects or surface imperfections and any mechanical damages were observed.
All measuring instruments/ equipment were verified for continued suitability for intended use, proper identification, calibration status, traceability to national standards & found satisfactory.

## Document reviewed
Document reviewed
QAP Sr. No. 1, 2 & 3 Reviewed Raw Material Test Certificate / Supplier Test certificate / test Reports for Body, Integral Ball with Stem and Lining as per relevant material specification / manufacturer standard and purchase order requirements - Found in order.
QAP Sr. No. 10 & 11 Painting and Marking Reports Reviewed as per approved Aarti Industries Purchase specification / Approved Drawing - Found in Order.
Reviewed calibration certificates of measuring instruments - Found in order to have valid calibration for intended use.

## Details of measuring instrument
Sr. No. | Detail of Equipment(s) / Instrument(s) | Range | ID | Validity till Date | Calibration Certificate Number | NABL / OTHER CERT. BODIES / NABL Traceability (type Yes wherever applicable) | NON-NABL (type Yes wherever applicable)
1 | Pressure Gauge | 0-60 Kg/Cm² | PG-55 | 21.06.2023 | HTA-2/0622/088 Dated 22.06.2022 |  | Yes | Yes
2 | Vernier Caliper | 0-300 mm | DVC-06 | 21.06.2023 | HTA-1/020721/069 Dated 06.07.2021 |  | Yes | No
3 | Measuring Tape | 0-5000 mm | MT-05 | 21.06.2023 | HTA-2/0622/115 Dated 22.06.2022 |  | Yes
4 | Digital Vernier Caliper | 0-300 mm | DVC-01 | 21.06.2023 | HTA-1/020721/001 Dated 06.07.2021 |  | Yes
5 | Pressure Gauge | 0-21 Kg/Cm² | PG-40 | 21.06.2023 | HTA-2/0622/194 Dated 30.06.2022 |  | Yes

## Areas of concerns
Areas Of Concern

## Pending Activities
Pending Activities from this visit
As per QAP Sr. No. 10, 11 & 12

## Conclusion
Note: Data filled in this sheet will not upload in TIIMES
Non Conformities raised / Discrepancies observed during Inspection (If Any, Mention TUV India NCR Number ):
Identification of Inspected Item(s):
Conclusion (Acceptable / Not Acceptable / Acceptance subject to):
IRN can be issued for PO Item numbers:
Expenses:
Remarks: