## Notes
Notes:
Data filled in General and conclusion Sections will not upload in TIIMES. Please use these sections to keep data ready for copy paste.
Data in Item Description columns of Accepted Quantity and cumulative Accepted quantity must be verified thoroughly before uploading in TIIMES.
Pending activity, Areas of concern & Details of measuring instruments sheets are applicable for IVR.
Select options from drop down list for unit of measurement (Item Description) & certifying body of measuring instruments (Details of measuring instruments).
Do not modify this format.
To start next row in cell itself use below shortcut: press 'alt + Enter' keys together. Alt + Enter

## General
Note: - Data filled in this sheet will not upload in TIIMES
Title | Details
Control Number
SAP number
Notification Number
Project Name & Location
Client Name
End User Name
DEC / PMC / EPC Name
DEC / PMC / EPC Number
Vendor Name
PO Number (Client PO on Vendor)
Sub Vendor
PO Number (Vendor PO on Sub Vendor)
Inspection Location
Inspection Date(s)

## Item Description
Po Item No. | Item Code | Item Description | Unit | Po Quantity | Offered Quantity | Accepted Quantity (Please verify thouroghly before using this Column for IRN) | Cumulative Accepted Quanitity (for IRN Only)
3 |  | MONITOR, WATER CUM FOAM/LONGRANGE, SIZE:4IN, MATERIAL:316 STAINLESS STEEL, SINGLE BARREL LEVER OPERATED, 500-750-1000 USGPM (VARIABLE FLOW),UL-162 STD, PROJECT CODE:500051 | number | 11 | 2 | 2 |  | number
meter
km
meter (number)
km (number)
each
Piece
Test sample
AU - All Unit
lot
Set
Running Meter
kg
metric ton (tonne)
ton
cubic millimetre
cubic centimeter
cubic meter
cubic inch
cubic foot
mm
cm
in
foot
mile
yard
liter
kl
cl
ml
g
lb
oz
Sq. mm
Sq. cm
Sq. meter
Sq. in
Sq. foot

## Reference Documents
Sr. No. | Document Name | Client Document Number | Vendor Document Number | Approval Status
1 | PR/MR/ARM | B224-CDU-TPL-000-TS-PR-0001 Rev.01 | Not Applicable | Approved
2 | QAP/ITP/QCP | B224­CDU­TPL­000­TS­QD PR0039­0001 Rev­02 | QAPNIS­9362, REV­02 (MONITOR) | Approved by CEIL
3 | Drawing(s) | B224­CDU­TPL­000­TS­GA PR0039­0002 Rev­02 (MONITOR) |  | Approved by EIL & FLOUR
4 | Procedure(s) | Not Applicable | Not Applicable | Not Applicable
5 | Datasheet(s) | B224­CDU­TPL­000­TS­DS PR0039­0002 Rev­02 (MONITOR) | Not Applicable | Approved by EIL & FLOUR
6 | Others (Specify) | Not Applicable | Not Applicable | Not Applicable

## Stages Witnessed
Stages Witnessed
Dimensional Inspection carried out on offered 02 Nos. monitors as per approved drawing ­ Dimensions found within tolerance limits.
Witnessed visual Inspection (on painted condition) on offered 02 Nos. monitors as per relevant standard ­ No major abnormalities or mechanical damage found, except see point mentioned in area of concern section.
Witnessed Performance Test at 7Kg/cm2 (g) (In Still Air­conditions) (Flow Test, Horizontal Water & Foam throw At 30°, 45°, 60° and Foam induction) ­ Found to meet the requirement.
Witnessed Nozzle Movement Verification on offered 02 Nos. monitors (Jet Mode and Spray Mode) ­ Found to meet the requirement.
Witnessed Monitor Movement {1) Horizontal Movement 360°manually by Hand wheel 2) Vertical Movement +90°,­45° manually by Hand wheel} ­ Found to meet the requirement.
Witnessed Hydro test on offered 02 Nos. monitors at 25 Kg/cm2 with 5 minutes holding time as per approved drawing and QAP ­ Neither leakage nor pressure drop observed during holding time.
Random Witnessed PMI Testing on offered 02 Nos. monitors as per approved drawing and QAP ­ found meeting requirements.
Witnessed painting inspection (DFT & Visual) on offered 02 Nos. monitors as per relevant standard requirement ­ Found to meet the requirements.
Witnessed marking verification on offered 02 Nos. monitors as per requirements ­ Found in order.

## Document reviewed
Document reviewed
Reviewed raw material test certificates for Base flange, Pipe, strainer, name plate, lifting hook, drain valve, swivel joint, worm, worm spindle, pick up tube, hand wheel, Elbow and nozzle as per relevant standard requirements ­ Found to meet the requirement.
Reviewed Internal Inspection report as per QAP ­ Found in order.
Reviewed calibration certificates being used during inspection ­ Found to meet the requirements.

## Details of measuring instrument
Sr. No. | Detail of Equipment(s) / Instrument(s) | Range | ID | Validity till Date | Calibration Certificate Number | NABL / OTHER CERT. BODIES / NABL Traceability (type Yes wherever applicable) | NON-NABL (type Yes wherever applicable)
1 | Pressure Gauge | 0 - 4.2 Kg/cm2 | NAFF/QAD/05 | 31.07.2023 | BCS/P/220801/12, Date: 01.08.2022 |  | Yes | Yes
2 | Measuring Tape | 0 to 5000 mm | MT02 | 16.03.2023 | CCS/22/S070/043, Date: 16.03.2022 | Yes |  | No
3 | Measuring Tape | 0 to 30000 mm | MT03 | 16.03.2023 | CCS/22/S070/044, Date: 16.03.2022 | Yes

## Areas of concerns
Areas Of Concern
Foam Tank: Stich Welding observed on wrapper plates (Shell to saddle weld): Client's Acceptance required
Fasteners: Fasteners MOC/Detailed Description not provided in approved drawings. However, at local portions short length Hex bolts observed & Hot Dip Galvanizing found damaged.: Vendor used Hex bolts as per their std. mfg. practice, replaced short length bolts with proper length Hex bolts, All Hex bolts found Hot dip galvanized at the time of inspection. However, Client's acceptance required for the same.
Skid Platform: Rust observed, Slag removal balance on welds, Weld defects observed. Cleaning and Rectification to be done and Re-offer for Visual and Dimensional Inspection.: Refer Dimension Report
Foam Skid Interconnecting Piping spools: Hydro test not offered to TPIA and EIL. Same witnessed by Vendor (M/s. New Age) only. Client to confirm.
As per EIL Comment No. 6: RT of Butt weld joints to be offered for review.: RT Films and Report reviewed for Monitor butt weld joints only and found in order. Client to confirm that Foam tank, interconnecting piping RT required or not?
Dimensional Inspection Foam Tank (Tag No. 101-V-172): Dimension Tolerance not provided in approved drawing. However, Measured dimensions are reported in dimension report. Client's acceptance required for the same.
Dimensional Inspection Skid Platform (Tag No. 101-FFS-102): Dimension Tolerance +5/-5% applicable for foundation holes ctr. To ctr. Client to confirm.
In-process stage inspection stages not offered for witness, details already mentioned in Previous Inspection visit report: Client's acceptance required.

## Pending Activities
Pending Activities from this visit
All other activities Mentioned above are Balance

## Conclusion
Note: Data filled in this sheet will not upload in TIIMES
Non Conformities raised / Discrepancies observed during Inspection (If Any, Mention TUV India NCR Number ):
Identification of Inspected Item(s):
Conclusion (Acceptable / Not Acceptable / Acceptance subject to):
IRN can be issued for PO Item numbers:
Expenses:
Remarks: