## Notes
Notes:
Data filled in General and conclusion Sections will not upload in TIIMES. Please use these sections to keep data ready for copy paste.
Data in Item Description columns of Accepted Quantity and cumulative Accepted quantity must be verified thoroughly before uploading in TIIMES.
Pending activity, Areas of concern & Details of measuring instruments sheets are applicable for IVR.
Select options from drop down list for unit of measurement (Item Description) & certifying body of measuring instruments (Details of measuring instruments).
Do not modify this format.
To start next row in cell itself use below shortcut: press 'alt + Enter' keys together. Alt + Enter

## General
Note: - Data filled in this sheet will not upload in TIIMES
Title | Details
Control Number
SAP number
Notification Number
Project Name & Location
Client Name
End User Name
DEC / PMC / EPC Name
DEC / PMC / EPC Number
Vendor Name
PO Number (Client PO on Vendor)
Sub Vendor
PO Number (Vendor PO on Sub Vendor)
Inspection Location
Inspection Date(s)

## Item Description
Po Item No. | Item Code | Item Description | Unit | Po Quantity | Offered Quantity | Accepted Quantity (Please verify thouroghly before using this Column for IRN) | Cumulative Accepted Quanitity (for IRN Only)
1 | 2002018502 | Hose NMET W CNN 0.75" ( 3/4") 300 PSI 15 Meter | number | 1 | 1 | 1 | 1 | number
2 | 2000205410 | Hose Flexme DN25, 20Kg/cm2, 10 Meter | number | 10 | 10 | 10 | 10 | meter
km
meter (number)
km (number)
each
Piece
Test sample
AU - All Unit
lot
Set
Running Meter
kg
metric ton (tonne)
ton
cubic millimetre
cubic centimeter
cubic meter
cubic inch
cubic foot
mm
cm
in
foot
mile
yard
liter
kl
cl
ml
g
lb
oz
Sq. mm
Sq. cm
Sq. meter
Sq. in
Sq. foot

## Reference Documents
Sr. No. | Document Name | Client Document Number | Vendor Document Number | Approval Status
1 | PR/MR/ARM | Not Applicable | Not Applicable | Not Applicable
2 | QAP/ITP/QCP | Not Applicable | QAP No.- Rev.0 Dt. 25.11.2022 | Approved by client in Email
3 | Drawing(s) | Not Applicable | JRE/RIL/01 REV.0 DT.25.11.2022 & JRE/RIL/02 REV.0 DT.25.11.2022 | Approved by client in Email
4 | Procedure(s) | Not Applicable | Not Applicable | Not Applicable
5 | Datasheet(s) | Not Applicable | Not Applicable | Not Applicable
6 | Others (Specify) | Not Applicable | Not Applicable | Not Applicable

## Stages Witnessed
Stages Witnessed
ITP Stage- 2 : Visual Inspection carried out for Hose randomly selected 10% Qty. (Min 01 No's.) for surface finish – No injurious surface defects were Observed.
ITP Stage- 2 : Dimension Inspection carried out for hose randomly selected 10% Qty. (Min 01 No's.) as per Drawing & QAP – Found to meet the Drawing requirements.
ITP Stage- 4 : ITP Stage- 4 : Hydro test carried out for Hose randomly selected 10% Qty. (Min 01 No's.) at 30 Kg/cm2 - No Leakage or pressure drop observed during holding time - Found Satisfactory
ITP Stage-5 : PMI witnessed for SS parts 10% Qty ( Min. 1 No.) from offered lot - Found to meet specification requirements
ITP Stage- 6: DP test witnessed for weld joints for inspected 10% Qty. (Min 01 No's.) – No recordable indication were Observed.
All measuring instruments/ equipment were verified for continued suitability for intended use, proper identification, calibration status, traceability to national standards & found satisfactory.

## Document reviewed
Document reviewed
ITP Stage 3 : Raw material test certificate of flange reviewed - Found to meet specification requirements.
ITP Stage-7 : Internal Inspection Reports, Works test/Guarantee certificates No.-219A & 219B Dtd. 20.02.2023 declared by supplier - Found to meet specification requirements
Calibration reports reviewed - Found to meet the code specification requirement.

## Details of measuring instrument
Sr. No. | Detail of Equipment(s) / Instrument(s) | Range | ID | Validity till Date | Calibration Certificate Number | NABL / OTHER CERT. BODIES / NABL Traceability (type Yes wherever applicable) | NON-NABL (type Yes wherever applicable)
1 | Measuring Tape | 0-30mtr | F-199-19 | 22.03.2023 | D-667 DT.23.3.2022 |  | Yes | Yes
2 | Pressure Gaue | 0-70 kg/cm2 | 3442 | 11.09.2023 | PG-8123 DT. 12.09.2022 |  | Yes | No
3 | Veriner Caliper | 0-300mm | SC50704170042 | 30.10.2023 | D-785 DT. 31.10.2022 |  | Yes
4 | Alloy Analyzer | -- | 811679 | 12.09.2023 | TII/CAL/AES/1133 DT. 13.09.2022 |  | Yes

## Areas of concerns
Areas Of Concern
None

## Pending Activities
Pending Activities from this visit
None

## Conclusion
Note: Data filled in this sheet will not upload in TIIMES
Non Conformities raised / Discrepancies observed during Inspection (If Any, Mention TUV India NCR Number ):
None
Identification of Inspected Item(s):
10 % inspected hose piped hard stamped as near manufacturer’s marking on flange OD. .
Conclusion (Acceptable / Not Acceptable / Acceptance subject to):
Acceptable
IRN can be issued for PO Item numbers:
Expenses:
Remarks: