## Notes
Notes:
Data filled in General and conclusion Sections will not upload in TIIMES. Please use these sections to keep data ready for copy paste.
Data in Item Description columns of Accepted Quantity and cumulative Accepted quantity must be verified thoroughly before uploading in TIIMES.
Pending activity, Areas of concern & Details of measuring instruments sheets are applicable for IVR.
Select options from drop down list for unit of measurement (Item Description) & certifying body of measuring instruments (Details of measuring instruments).
Do not modify this format.
To start next row in cell itself use below shortcut: press 'alt + Enter' keys together. Alt + Enter

## General
Note: - Data filled in this sheet will not upload in TIIMES
Title | Details
Control Number
SAP number
Notification Number
Project Name & Location
Client Name
End User Name
DEC / PMC / EPC Name
DEC / PMC / EPC Number
Vendor Name
PO Number (Client PO on Vendor)
Sub Vendor
PO Number (Vendor PO on Sub Vendor)
Inspection Location
Inspection Date(s)

## Item Description
Po Item No. | Item Code | Item Description | Unit | Po Quantity | Offered Quantity | Accepted Quantity (Please verify thouroghly before using this Column for IRN) | Cumulative Accepted Quanitity (for IRN Only)
1 | CH000071815 | PVDF AODD PUMP 1/1/1m³/h 30m 100% , Indent/PR : 23055084-10, Make & Model : BLAGDON | number | 1 | 1 | 1 | 1 | number
meter
km
meter (number)
km (number)
each
Piece
Test sample
AU - All Unit
lot
Set
Running Meter
kg
metric ton (tonne)
ton
cubic millimetre
cubic centimeter
cubic meter
cubic inch
cubic foot
mm
cm
in
foot
mile
yard
liter
kl
cl
ml
g
lb
oz
Sq. mm
Sq. cm
Sq. meter
Sq. in
Sq. foot

## Reference Documents
Sr. No. | Document Name | Client Document Number | Vendor Document Number | Approval Status
1 | PR/MR/ARM | Not Applicable | Not Applicable | Not Applicable
2 | QAP/ITP/QCP | PIN-056-M1-4550355857-MEC-K01-001, Rev. A | 11/2021 | Approved by M/s Samtech Engineering Services Pvt Ltd.
3 | Drawing(s) | PIN-056-M1-4550355857-MEC-F01-001, Rev. B | S1501KTBBTTK-AODD Pump, Rev.1 | Approved by M/s Techin Process Technologies Pvt. Ltd.
4 | Procedure(s) | Not Applicable | Not Applicable | Not Applicable
5 | Datasheet(s) | Not Applicable | Not Applicable | Not Applicable
6 | Others (Specify) | Not Applicable | Not Applicable | Not Applicable

## Stages Witnessed
Stages Witnessed
QAP Sr. No. 2; (a) Hydro test at a pressure of 4 kg/cm² (g) [Required test pressure: 5 kg/cm² (g)] for a holding time of 30 minutes – No Leakage / No pressure drop observed during holding time. (b) Noise level check witness – found to mee the standard requirements.
QAP Sr. No. 3; (a) Pump assembly overall dimension checked – Found as per drawing. (b) Visual inspection carried out – No injurious surface imperfections or sharp edges were observed
QAP Sr. No. 4; Performance (Flow v/s. Head) test witness as per approved QAP/ITP – found to meet the standard requirements.

## Document reviewed
Document reviewed
QAP Sr. No. 1; Compliance certificate for Materials – Found in order.

## Details of measuring instrument
Sr. No. | Detail of Equipment(s) / Instrument(s) | Range | ID | Validity till Date | Calibration Certificate Number | NABL / OTHER CERT. BODIES / NABL Traceability (type Yes wherever applicable) | NON-NABL (type Yes wherever applicable)
1 | Water Flow Meter | 0 - 240 GPM | 61311060606 | 17/11/2022 | CC/2105652, Dated 18-11-2021 | Yes |  | Yes
2 | Air Flow Meter | 1 - 80 scfm | 34461 | 17/11/2022 | CC/21/11/00011, Dated 18-11-2021 |  | Yes | No
3 | Pressure Gauge | 0 - 28 kg/cm2(g) | 18KD3344 | 14/02/2022 | GMGS/N0539/2021, Dated 15-02-2021 | Yes
4 | Pressure Gauge | 0 - 16 kg/cm2(g) | SG160310759 | 15/07/2022 | GMGS/N1427/2021, Dated 16-07-2021 | Yes
5 | Sound Level Meter | 40 - 130 dB | 10026006 | 28/09/2022 | GMGS/1270/2021, Dated 29-09-2021 |  | Yes
6 | Pressure Gauge | 0 - 16 kg/cm2(g) | 90279233-1-3 | 15/07/2022 | GMGS/N1426/2021, Dated 16-07-2021 | Yes
7 | Vernier Caliper | 0 - 150 mm | A19248878 | 2022-09-12 | GMGS/N2893/2021, Dated 10-12-2021 | Yes
8 | Measuring Tape | 0 - 5 m | MT-01 | 2022-09-05 | GMGS/N0889/2021, Dated 10-05-2021 | Yes

## Areas of concerns
Areas Of Concern

## Pending Activities
Pending Activities from this visit

## Conclusion
Note: Data filled in this sheet will not upload in TIIMES
Non Conformities raised / Discrepancies observed during Inspection (If Any, Mention TUV India NCR Number ):
Identification of Inspected Item(s):
Conclusion (Acceptable / Not Acceptable / Acceptance subject to):
IRN can be issued for PO Item numbers:
Expenses:
Remarks: