## Notes
Notes:
Data filled in General and conclusion Sections will not upload in TIIMES. Please use these sections to keep data ready for copy paste.
Data in Item Description columns of Accepted Quantity and cumulative Accepted quantity must be verified thoroughly before uploading in TIIMES.
Pending activity, Areas of concern & Details of measuring instruments sheets are applicable for IVR.
Select options from drop down list for unit of measurement (Item Description) & certifying body of measuring instruments (Details of measuring instruments).
Do not modify this format.
To start next row in cell itself use below shortcut: press 'alt + Enter' keys together. Alt + Enter

## General
Note: - Data filled in this sheet will not upload in TIIMES
Title | Details
Control Number
SAP number
Notification Number
Project Name & Location
Client Name
End User Name
DEC / PMC / EPC Name
DEC / PMC / EPC Number
Vendor Name
PO Number (Client PO on Vendor)
Sub Vendor
PO Number (Vendor PO on Sub Vendor)
Inspection Location
Inspection Date(s)

## Item Description
Po Item No. | Item Code | Item Description | Unit | Po Quantity | Offered Quantity | Accepted Quantity (Please verify thouroghly before using this Column for IRN) | Cumulative Accepted Quanitity (for IRN Only)
|  | 3591015583 dated 11.11.2022 ( Hitachi energy to 3D Fire ) | [5 empty] | number
1 | NA | End suction Pump CPHM 150/43 with Motor driven, Capacity- 273 M3/hr, Pump Sr No.- | number | 1 | 1 | Refer Conclusion |  | meter
2 | NA | End suction Pump CPHM 150/43 with Engine driven ,Capacity - 273 M3/hr, Pump Sr No.- | number | 1 | 1 | Refer Conclusion |  | km
3 | NA | End suction Pump CPHM 25/26A with Motor driven, Capacity - 10.38 M3/hr, Pump Sr No.- | number | 1 | 1 | Refer Conclusion |  | meter (number)
km (number)
each
Piece
Test sample
AU - All Unit
lot
Set
Running Meter
kg
metric ton (tonne)
ton
cubic millimetre
cubic centimeter
cubic meter
cubic inch
cubic foot
mm
cm
in
foot
mile
yard
liter
kl
cl
ml
g
lb
oz
Sq. mm
Sq. cm
Sq. meter
Sq. in
Sq. foot

## Reference Documents
Sr. No. | Document Name | Client Document Number | Vendor Document Number | Approval Status
1 | PR/MR/ARM | NA | NA | NA
2 | QAP/ITP/QCP | NA | For Motor driven pump:- QAP/01/F08323A510/MD REV 00 , Engine Driven Pump:- QAP/01/F08323A510/ED REV 00 | Hitachi Engergy Pvt Ltd
3 | Drawing(s) | NA | CSD:- TC781519664-0, TC781519667-0, TC781519678-0, GA Drawing:- TF781519664-0, TF17822024-0, TF781519678-0 | Hitachi Engergy Pvt Ltd
4 | Procedure(s) | NA | NA | NA
5 | Datasheet(s) | NA | HD13764KB0 REV 0, HD13764KB0 REV 0, HD13793AA0 REV 0 | Hitachi Engergy Pvt Ltd
6 | Others (Specify) | NA | NA | NA

## Stages Witnessed
Stages Witnessed
QAP Clause No.- 3.1 Witness performance testing of pump with job motor for Model CPHM 150/43 Pump Sr No.- 178433014 & CPHM 25/26A Pump Sr No.- 1789323128 Checked Flow (Q) vs Head (H), flow vs Efficiency , Flow vs Power parameter with respect to datasheet & perfromace curve & found satisfactory
QAP Clause No.- 3.1 Witness performance testing of pump with job Diesel Engine for Model CPHM 150/43 Pump Sr No.- 178433013 checked Flow (Q) Vs Head (H) parameter with respect to datasheet & perfromace curve & found satisfactory
QAP Clause No.- 3.1 Witness MRT of pumps witn Job motor Model CPHM 150/43 Pump Sr No.- 178433014 & CPHM 25/26A Pump Sr No.- 1789323128 & Model CPHM 150/43 Engine Driven pump Sr No.- 178433013 checked speed, vibartion, noise level & bearing oil tempertaure of pump & found satisfactory

## Document reviewed
Document reviewed
For Engine Driven pump & Motor Driven pump
QAP Sr No.-1.1,1.2 Review material compliance certificates of casing, impeller, shaft as per drawing & found satisfactory
QAP Sr No. 2.1 - Impeller dynamic Balancing report reviewed & found accepted
QAP Sr No. 2.2 - Hydro Test Report reviewed of casing and found accepted.
QAP Sr No.3 1 & 3.1 - Pump Performance Test report reviewed and found accepted
Review Engine driven performance report with shop motor as per QAP & Datasheet & found satisfactory
Calibration of Instruments Sheet & Calibration Certificate reviewed and found satisfactory

## Details of measuring instrument
Sr. No. | Detail of Equipment(s) / Instrument(s) | Range | ID | Validity till Date | Calibration Certificate Number | NABL / OTHER CERT. BODIES / NABL Traceability (type Yes wherever applicable) | NON-NABL (type Yes wherever applicable)
| As attached | [6 empty] | Yes
No

## Areas of concerns
Areas Of Concern
1) Motor Driven pump CPHM 150/43 & CPHM 25/26A- In datasheet motor make- CGL mentioned & GA drawing, motor make- BBL mentioned however vendor offered BBL make motor for pumps
2) Diesel engine & Job motor TPI or customer IRN or IVR to be submitted for review
3) GA drawing Tag number not mentioned pumps
4) In CSD of CPHM 150/43 & CPHM 25/26A pumps, casing cover MOC CI IS 210 FG 260 mentioned however M/s KBL offered CI IS 210FG 260 Ni 2.5 MOC casing cover

## Pending Activities
Pending Activities from this visit

## Conclusion
Note: Data filled in this sheet will not upload in TIIMES
Non Conformities raised / Discrepancies observed during Inspection (If Any, Mention TUV India NCR Number ):
Identification of Inspected Item(s):
Conclusion (Acceptable / Not Acceptable / Acceptance subject to):
Inspection found acceptable except mentioned in area of concern
IRN can be issued for PO Item numbers:
Expenses:
Remarks: