## Notes
Notes:
Data filled in General and conclusion Sections will not upload in TIIMES. Please use these sections to keep data ready for copy paste.
Data in Item Description columns of Accepted Quantity and cumulative Accepted quantity must be verified thoroughly before uploading in TIIMES.
Pending activity, Areas of concern & Details of measuring instruments sheets are applicable for IVR.
Select options from drop down list for unit of measurement (Item Description) & certifying body of measuring instruments (Details of measuring instruments).
Do not modify this format.
To start next row in cell itself use below shortcut: press 'alt + Enter' keys together. Alt + Enter

## General
Note: - Data filled in this sheet will not upload in TIIMES
Title | Details
Control Number
SAP number
Notification Number
Project Name & Location
Client Name
End User Name
DEC / PMC / EPC Name
DEC / PMC / EPC Number
Vendor Name
PO Number (Client PO on Vendor)
Sub Vendor
PO Number (Vendor PO on Sub Vendor)
Inspection Location
Inspection Date(s)

## Item Description
Po Item No. | Item Code | Item Description | Unit | Po Quantity | Offered Quantity | Accepted Quantity (Please verify thouroghly before using this Column for IRN) | Cumulative Accepted Quanitity (for IRN Only)
1 | S041139-401 | Carbon Steel Seamless Cold Drawn Straight Tubes as per SA 179M of ASME Sec II Part­ A Edition 2021.(IBR as per ARM) Size: 25.00 mm OD X 2.20 mm THK (Min) X 4950 mm Long, Heat No: 3225234. | number | 258 Nos. | 258 Nos. | 258 Nos. | 258 Nos. | number
4 | S041139-496 | Carbon Steel Seamless Cold Drawn Straight Tubes as per SA 179M of ASME Sec II Part­ A Edition 2021.(IBR as per ARM) Size: 25.00 mm OD X 2.20 mm THK (Min) X 3200 mm Long, Heat No: 3225234. | number | 2 Nos. | 2 Nos. | 2 Nos. | 2 Nos. | meter
6 | S041139-498 | Carbon Steel Seamless Cold Drawn Straight Tubes as per SA 179M of ASME Sec II Part­ A Edition 2021.(IBR as per ARM) Size: 25.00 mm OD X 2.20 mm THK (Min) X 3500 mm Long, Heat No: 3225234. | number | 2 Nos. | 2 Nos. | 2 Nos. | 2 Nos. | km
meter (number)
km (number)
each
Piece
Test sample
AU - All Unit
lot
Set
Running Meter
kg
metric ton (tonne)
ton
cubic millimetre
cubic centimeter
cubic meter
cubic inch
cubic foot
mm
cm
in
foot
mile
yard
liter
kl
cl
ml
g
lb
oz
Sq. mm
Sq. cm
Sq. meter
Sq. in
Sq. foot

## Reference Documents
Sr. No. | Document Name | Client Document Number | Vendor Document Number | Approval Status
1 | PR/MR/ARM | ADDITIONAL REQUIREMENT OF MATERIALS : 41139961 R1, DATED: 17.04.2023. | NOT APPLICABLE | Client Document.(Larsen & Toubro Limited.)
2 | QAP/ITP/QCP | NOT APPLICABLE | QAP No: RMTL/C-4366/23-24, DATED: 22.04.2023. | Approved by Client.(Larsen & Toubro Limited.)
3 | Drawing(s) | NOT APPLICABLE | NOT APPLICABLE | NOT APPLICABLE
4 | Procedure(s) | NOT APPLICABLE | 1) Procedure for EDDY Current Testing of Carbon Steel & Low Alloy Steel Tubes / Pipes using through coil method: RMTL/ECT/L&T/C-4366/01 REV.03, DATED: 19.06.2023. 2) Procedure for hydro testing and drying & cleaning of tubes/pipes of carbon steel & low alloy steel: RMTL/HYDRO/L&T/C-4366/02 Rev.0, Dated:12.05.2023. | Approved by Client.(Larsen & Toubro Limited.)
5 | Datasheet(s) | NOT APPLICABLE | NOT APPLICABLE | NOT APPLICABLE
6 | Others (Specify) | NOT APPLICABLE | NOT APPLICABLE | NOT APPLICABLE

## Stages Witnessed
Stages Witnessed
Sampling has been carried out for Chemical & Mechanical test (Tesnile Test, Hardness Test & Flaring Test, Flattening Test) for testing as per approved QAP­Found in order.
QAP Sr No. 4: Witnessed Mechanical test (Tesnsile Test, Hardness Test, Flaring Test & Flattening Test) at at inhouse Testing Lab-Found to meet the specification requirements.
QAP Sr No 5: Witnessed Eddy current test on 100% qty of Straight Tubes in random length as per E 309 & Acceptance standard SA 450M as per approved QAP–No recordable discontinuity observed Hence Found Satisfactory.
QAP Sr No. 6: Witnessed Hydrostatic test on 100% Quantity of tubes in random length at 100 Kg/cm2 (g) pressure as per approved QAP & ARM- No pressure drop or no any leakage observed during holding time minimum 15 second.Chloride Content less then 25 PPM.
QAP Sr No. 7: Witnessed drying & sponge passing inside tubes after hydro test as per approved QAP-Found Satisfactory.
QAP Sr No.8: Witnessed DP test on both end ID, OD & face in final length (both end polissed) at accesible area for 100% Qty. of Tubes as per approved QAP & ARM-Found Satisfactory.
QAP Sr No.9: Visual inspection for surface finish carried out for 100% quantity of tubes in final length at accessible area as per approved QAP­No injurious surface defect observed.
QAP Sr No. 9: Witnessed dimensional inspection for 100% quantity of tubes in final length as per approved QAP­Dimensions found within tolerance limit.
QAP Sr No. 10: Verified product marking on 100% quantity of Tube as per approved QAP­Found satisfactory.
All measuring instruments/ equipment were verified for continued suitability for intended use, proper identification, calibration status, traceability to national standards & found satisfactory.

## Document reviewed
Document reviewed
QAP Sr No. 1: Reviewed Copy of Raw material test certificates as declared by vendor as per approved QAP­Found to meet the specification requirements.
QAP Sr No. 2 : Reviewed Heat treatment chart / record as per approved QAP­Found in order.
QAP Sr No. 3: Reviewed Chemical Test (Product Analysis) Report for inhouse lab as per approved QAP­Found in order.
QAP Sr No.11: Reviewed Packing list (end protection cap & wooden box) report as approved QAP--​Found in order.
QAP Sr No. 12: Reviewed manufacturer's inspection test certificate (EN­10204­3.2) No: RMTL/CS­307/23­24, Dated: 08.08.2023 as per approved QAP­Found in order.
Reviewed Calibration certificate copy-Found in order.

## Details of measuring instrument
Sr. No. | Detail of Equipment(s) / Instrument(s) | Range | ID | Validity till Date | Calibration Certificate Number | NABL / OTHER CERT. BODIES / NABL Traceability (type Yes wherever applicable) | NON-NABL (type Yes wherever applicable)
1 | Digital Pressure Gauge | 0-250 Bar | 1910173-738311 | 13.08.2023 | CC100423000000191F | Yes |  | Yes
2 | Thickness Micrometer | 0-25 MM | S/N -86571043 | 02.08.2023 | CC100422000000727F | Yes |  | No
3 | External Micrometer | 0-25 MM | S/N- 16015464 | 02.08.2023 | CC100422000000713F | Yes
4 | Measuring Tape | 0-15 MTR | M-Tape-A-01 | 04.01.2024 | CC100423000000009F | Yes

## Areas of concerns
Areas Of Concern
None.

## Pending Activities
Pending Activities from this visit
As per approved QAP.

## Conclusion
Note: Data filled in this sheet will not upload in TIIMES
Non Conformities raised / Discrepancies observed during Inspection (If Any, Mention TUV India NCR Number ):
Identification of Inspected Item(s):
Conclusion (Acceptable / Not Acceptable / Acceptance subject to):
IRN can be issued for PO Item numbers:
Expenses:
Remarks: