## Notes
Notes:
Data filled in General and conclusion Sections will not upload in TIIMES. Please use these sections to keep data ready for copy paste.
Data in Item Description columns of Accepted Quantity and cumulative Accepted quantity must be verified thoroughly before uploading in TIIMES.
Pending activity, Areas of concern & Details of measuring instruments sheets are applicable for IVR.
Select options from drop down list for unit of measurement (Item Description) & certifying body of measuring instruments (Details of measuring instruments).
Do not modify this format.
To start next row in cell itself use below shortcut: press 'alt + Enter' keys together. Alt + Enter

## General
Note: - Data filled in this sheet will not upload in TIIMES
Title | Details
Control Number | 50206304521
SAP number | 8119528802
Notification Number | Email Dt 10.12.2021
Project Name & Location | Assam Bio Refinery Project
Client Name | Assam Bio Refinery Private Limited
End User Name | Assam Bio Refinery Private Limited
DEC / PMC / EPC Name | Engineers India Ltd
DEC / PMC / EPC Number
Vendor Name | Baliga Lighting Equipments Pvt Ltd
PO Number (Client PO on Vendor) | ABRPL/DPO/HAZ.AREA Equipment /094 dt
Sub Vendor | None
PO Number (Vendor PO on Sub Vendor) | Not Applicable
Inspection Location | Baliga Lighting Equipemnts Pvt. Ltd., Kovilambakkam
Inspection Date(s) | 11.12.2021

## Item Description
Po Item No. | Item Code | Item Description | Unit | Po Quantity | Offered Quantity | Accepted Quantity (Please verify thouroghly before using this Column for IRN) | Cumulative Accepted Quanitity (for IRN Only)
1.01 | FLPW-1095 | Ex-d, GRP IIA/IIB, T3, Well glass, 6000-6500 Lumens, 100LM/W, LTG Fixture & Acc complete with LED lamp, Sl Nos: | number | 2800 | 750 | 750 | 1240 | number
1.03 | FLP-LED2-IIA/IIB | Ex-d, GRP IIA/IIB, T3, Well glass, 10000-10500 Lumens, 100LM/W, LTG Fixture & Acc complete with LED lamp | number | 300 | 8 | 8 | 170 | meter
1.05 | FLP-LED-FD2 IIA/IIB | Ex-d, GRP IIA/IIB, T3, Flood Light, 10000-10500 Lumens, 100LM/W, LTG Fixture & Acc complete with LED lamp | number | 100 | 28 | 28 | 100 | km
1.11 | SOCKET3-IIA/IIB | Ex-d, GRP IIA/IIB, T3, Socket,240V-3 PIN-15A | number | 120 | 120 | 120 | 120 | meter (number)
1.13 | SOCKET5-IIA/IIB | Ex-d, GRP IIA/IIB, T3, Socket,415V-5 PIN-63A | number | 20 | 20 | 20 | 20 | km (number)
1.21 | PB-C1-IIA/IIB | LCS with start & Stop PB& ammeter.Exd,GRP IIA/IIB,T3 | number | 35 | 32 | 32 | 32 | each
1.23 | PB-I-E1-IIA/IIB | LCS with start & Stop PB with L-O-R switch & Ammeter Ex-d,GRP IIA/IIB,T3 | number | 80 | 33 | 33 | 33 | Piece
1.25 | PB-I-B-IIA/IIB | LCS with close PB,Red Color ,EEXd type,gasgroup IIA/IIB T3 | number | 5 | 5 | 5 | 5 | Test sample
1.28 | SEL-SW2-1-IIA/B | LCS With2 position selector switch,Eexd,GRP IIA/IIB,T3,1A,24V DC | number | 10 | 10 | 10 | 10 | AU - All Unit
lot
Set
Running Meter
kg
metric ton (tonne)
ton
cubic millimetre
cubic centimeter
cubic meter
cubic inch
cubic foot
mm
cm
in
foot
mile
yard
liter
kl
cl
ml
g
lb
oz
Sq. mm
Sq. cm
Sq. meter
Sq. in
Sq. foot

## Reference Documents
Sr. No. | Document Name | Client Document Number | Vendor Document Number | Approval Status
1 | PR/MR/ARM
2 | QAP/ITP/QCP | 6-81-1006 Rev 4 , 6-81-1021, Rev.3, 6-81-1061, Rev.4 | 6-81-1006 Rev 4 , 6-81-1021, Rev.3, 6-81-1061, Rev.4 | M/s EIL Standard ITP
3 | Drawing(s) | CE210174 01, Rev.5, CE21017413, Rev.2, CE21017403, Rev.4, CE210174 22 Rev.2, | CE210174 01, Rev.4 CE210174 13, Rev.2 , CE210174 03, Rev.3, CE210174 22, Rev.4, | Code-R by M/s EIL Dt.03/Nov/2021 Code-R by M/s EIL Dt.06/Dec/2021 Code-R by M/s EIL Dt.16/Nov/2021 Code-1 by M/s EIL Dt.06/DEC/2021
4 | Procedure(s)
5 | Datasheet(s)
6 | Others (Specify)

## Stages Witnessed
Stages Witnessed
As per QAP 100% witnessed on the offered Flame control stations .
As per ITP Clause 4.1- below activities carried out on the offered power panels: a) Visual inspection of enclosure for finish, Clear printing of Serial No, Certification Marking, Finish of Gaskets, Din Rails, Terminals, Earthing & BOM Check carried out on the Offered Local Control Stations as per approved drawings- Found Satisfactory. b) Mounting/Overall dimensional check carried out for length, width, height of the enclosures, thickness of the canopy- Found Satisfactory. c) Wiring Checked and Found as per approved drawing. d) Paint shade, adhesion and thickness verified and found satisfactory. e) Mechanical and electrical operations verified and found satisfactory. f) Witnessed HV test (test voltage 2 kV AC for 1minute)- Found withstood the same. g) Flame gap/path verified and found satisfactory. h) Witnessed insulation resistance test (before & after H.V test)- Found the insulation resistance values are more than 100 Mega Ohms (Test Voltage 500V DC). i) Name plate and tag plates verified- Found meeting the drawing requirements.

## Document reviewed
Document reviewed
As per ITP Clause 4.1: Reviewed below tests Internal Inspection Reports for the offered Lighting Fixtures & Junction Boxes :- a) Physical, Dimensional and BOM Verification. b) Flame paths & Clearances. c) Marking on each piece for suitability to area classification, Tag No. and other details as per relevant IS/IEC. d) Impact test (on samples) e) Thermal shock test (on samples) f) Functional Check g) Power factor test on driver h) HV Test i) IR Test before and after HV - Found in order and attested for records.
As per ITP Clause 4.1: Reviewed below tests Internal Inspection Reports for the offered Flame Proof Plugs & Sockets :- a) Visual check b) Dimensional (Flame path/gap/clearances etc.) c) Bill of Materials checks d) Compatibility of cable glands with cable sizes/cable entry e) Verification of mechanical & electrical operation f) HV test / Insulation Resistance test before and after HV test g) Colour of metal enclosures. -Found acceptable
As per ITP Clause 4.1: Reviewed below tests Internal Inspection Reports for the offered Hazardous Area lighting fixures:- a) Physical and Dimension and BOM verification b) Flame path/gap/clearances etc. c) Marking on each peice for suitablity to arae classification ,tag No and other details as per IS/IEC . d) marking on glass for type and other detais as per IS/IEC e) Test for restricted breathing enclosure for div 2 f) impact test on sample g) thermal shock test ( on sam-les) h) electrical operation check i) HV test / Insulation Resistance test before and after HV test -Found acceptable
As per ITP Clause 2: Reviewed raw materials test certificates of LM6 (Enclosure), Electrical Components, Gaskets, Fasteners, Cable glands & Stopping plugs of the offered items- Found in order and attested for records.
As per ITP Clause 2.1: Reviewed manufacturer quality assurance certificate & internal inspection report of the offered items- Found in order and attested for records.
As per ITP Clause 3.1: Reviewed flame proof enclosure without components Routine Pressure test report -found acceptable and reports attested for records.
As per ITP Clause 4.2: Reviewed type approval certificates (CIMFR, PESO & BIS) for the offered items- Found in order and reports attested for records.
Verified Calibration Status of the instruments used for inspection- Found valid calibration and attested for records.

## Details of measuring instrument
Sr. No. | Detail of Equipment(s) / Instrument(s) | Range | ID | Validity till Date | Calibration Certificate Number | NABL / OTHER CERT. BODIES / NABL Traceability (type Yes wherever applicable) | NON-NABL (type Yes wherever applicable)
1 | AC High Voltage Tester | 0-3kV | S1907022 | 2022-03-03 | MSIR/410321/39003 | Yes |  | Yes
2 | Digital Insulation Tester | 1000 M ohm | 1907003642 | 2022-09-03 | MSIR/410921/28001 | Yes |  | No
3 | Vernier Caliper | 0-300mm | 12330001 | 2022-08-12 | 04-120821-003 | Yes

## Areas of concerns
Areas Of Concern
nil

## Pending Activities
Pending Activities from this visit
nil

## Conclusion
Note: Data filled in this sheet will not upload in TIIMES
Non Conformities raised / Discrepancies observed during Inspection (If Any, Mention TUV India NCR Number ):
Identification of Inspected Item(s):
Conclusion (Acceptable / Not Acceptable / Acceptance subject to):
IRN can be issued for PO Item numbers:
Expenses:
Remarks: