## Notes
Notes:
Data filled in General and conclusion Sections will not upload in TIIMES. Please use these sections to keep data ready for copy paste.
Data in Item Description columns of Accepted Quantity and cumulative Accepted quantity must be verified thoroughly before uploading in TIIMES.
Pending activity, Areas of concern & Details of measuring instruments sheets are applicable for IVR.
Select options from drop down list for unit of measurement (Item Description) & certifying body of measuring instruments (Details of measuring instruments).
Do not modify this format.
To start next row in cell itself use below shortcut: press 'alt + Enter' keys together. Alt + Enter

## General
Note: - Data filled in this sheet will not upload in TIIMES
Title | Details
Control Number
SAP number
Notification Number
Project Name & Location
Client Name
End User Name
DEC / PMC / EPC Name
DEC / PMC / EPC Number
Vendor Name
PO Number (Client PO on Vendor)
Sub Vendor
PO Number (Vendor PO on Sub Vendor)
Inspection Location
Inspection Date(s)

## Item Description
Po Item No. | Item Code | Item Description | Unit | Po Quantity | Offered Quantity | Accepted Quantity (Please verify thouroghly before using this Column for IRN) | Cumulative Accepted Quanitity (for IRN Only)
000 04 | -- | E-3301 Primary Condenser for R-3302 | each | 1 | 1 | 1 | 1 | number
000 13 | -- | E-3312 Complete CAC Rec Reactor Reboiler | each | 1 | 1 | 1 | 1 | meter
km
meter (number)
km (number)
each
Piece
Test sample
AU - All Unit
lot
Set
Running Meter
kg
metric ton (tonne)
ton
cubic millimetre
cubic centimeter
cubic meter
cubic inch
cubic foot
mm
cm
in
foot
mile
yard
liter
kl
cl
ml
g
lb
oz
Sq. mm
Sq. cm
Sq. meter
Sq. in
Sq. foot

## Reference Documents
Sr. No. | Document Name | Client Document Number | Vendor Document Number | Approval Status
1 | PR/MR/ARM | Not Applicable | Not Applicable | Not Applicable
2 | QAP/ITP/QCP | Not Applicable | GIL/STD QAP/UPL/01 Rev - 00 | Approved by Client representative Mr. Mehul Mehta on Dtd.-07.04.2022.
3 | Drawing(s) | Not Applicable | 1) GV/33960/21 Rev - 01 2) GV/33969/21 Rev - 01 | Approved by Mott Macdonald Pvt. Ltd.
4 | Procedure(s) | Not Applicable | Not Applicable | Not Applicable
5 | Datasheet(s) | Not Applicable | Not Applicable | Not Applicable
6 | Others (Specify) | Not Applicable | Not Applicable | Not Applicable

## Stages Witnessed
Stages Witnessed
For Tag Nos. E-3301, E-3312 Assembled equipments witnessed for below mentioned activities:
As per QAP Stage A-3 : Pneumatic test witnessed of graphite block 10% randomly selected block at 8 Kg/cm2g for 20 minutes duration - No leakage/bubbles or pressure drop observed during testing period.
As per QAP Clause No D - (a).
A) Dimensional Inspection of Graphite Equipment Witnessed. B) Dimensions for Shell total length, height, ODCF, Nozzle projections, Elevation, Nozzle orientation, Nozzle size witnessed - found as per drawing & within given tolerance. C) Dimensions for Equipment Mouting / Foundation details (i.e C/C Distance, Hole Dia, Slot Size, base plate size, elevation etc.) witnessed - found as per drawing. D) Other dimensions mentioned in drawing witnessed - found as per drawing.
As per QAP Clause No D - (b).
A) Graphite Equipments Process side Hydro test witnessed at a pressure 8 kg/cm2 for a pressure holding period of 30 minutes (minimum) as mentioned in the drawing - No leakages / No pressure drop observed during pressure holding time – Test found Satisfactory. B) Graphite Equipments Service side Hydro test witnessed at a pressure 8 kg/cm2 for a pressure holding period of 30 minutes (minimum) as mentioned in the drawing - No leakages / No pressure drop observed during pressure holding time – Test found Satisfactory. C) Graphite Equipment offered for Hydrotest is in Final Painted Condition except pressure part weld joints.
A) Visual Inspection for Graphite Equipment in Final Painted condtion for outer surface & for internal surface upto accessible area carried out, Workmanship Found Satisfactory. B) Equipment is in final painted condition during visual inspection.
As per QAP Clause no. G Spare verified for all equipments witnessed as per spare list provided by vendor - Found in order.
All measuring instruments/ equipment were verified for continued suitability for intended use, proper identification,calibration status, traceability to national standards & found satisfactory.

## Document reviewed
Document reviewed
For Tag Nos. E-3301, E-3312, equipments reviewed for below mentioned activities:
As per QAP Stage A-1 : Raw material for graphite component declaration for graphite properties inspection report reviewed as provided by supplier - Found in order.
As per QAP Stage A-2 : Grahite blocks in process visual & dimensional inspection report reviewed as provided by supplier - Found in order.
As per QAP Stage A-3 : Pneumatic test of graphite blocks and end chambers inspection report reviewed as provided by supplier - Found in order.
As per QAP Clause No B. MTC / Lab TC Photocopy for fasteners & steel parts as provided by vendor reviewed , values given the TC are acceptable as per material specification requirement, hence TC's are found in order.
As per QAP Clause No B-2. Material Heat chart for steel parts as declared by supplier reviewed - found as acceptable as per material specification requirement and approved drawing requirement.
As per QAP Clause No B-3: i) RT report for tag no. E-3302, PO Sr no. 0005 as provided by vendor reviewed - Found in order. Ii) For rest of the equipments/ PO Sr no. RT is not applicable as shell made up of pipe and no any butt weld joint for shell.
UT report for butt welb joints as provided by vendor reviewed - Found in order.
As per QAP Clause No B-4 Final inspection report of fabricated component for Visual , Dimension & pressure test as provided by vendor reviewed - Found in order.
As per QAP Clause no. C Blasting and painting report submitted for review - Found in order as per drawing, QAP requiremement.
As per QAP Clause no. E Final painting report submitted for review - Found in order as per drawing, QAP requiremement.
As per QAP Clause no. F PTFE Bellows internal inspection report i.e. hydro test and dimensional reviewed as provided by vendor - Found in order.
Calibration certificates of measuring instruments used for inspection are reviewed - found in order.

## Details of measuring instrument
Sr. No. | Detail of Equipment(s) / Instrument(s) | Range | ID | Validity till Date | Calibration Certificate Number | NABL / OTHER CERT. BODIES / NABL Traceability (type Yes wherever applicable) | NON-NABL (type Yes wherever applicable)
1 | Vernier Caliper | 0 - 300 mm | GV - 65 | 03.01.2023 | GV 65 Date : 03.01.2022 |  | Yes | Yes
2 | Pressure Guage | 0 - 16 Kg/cm2 | GV - 02 | 20.04.2022 | GV - 02 Date : 20.03.2022 |  | Yes | No
3 | Pressure Guage | 0 - 16 Kg/cm2 | GV - 21 | 10.04.2022 | GV - 21 Date : 10.03.2022 |  | Yes
4 | Pressure Guage | 0 - 16 Kg/cm2 | GV - 26 | 10.04.2022 | GV - 26 Date : 10.03.2022 |  | Yes
5 | Pressure Guage | 0 - 16 Kg/cm2 | GV - 20 | 10.04.2022 | GV - 20 Date : 10.03.2022 |  | Yes
6 | Pressure Guage | 0 - 16 Kg/cm2 | GV - 52 | 10.04.2022 | GV - 52 Date : 10.03.2022 |  | Yes
7 | Pressure Guage | 0 - 16 Kg/cm2 | GV - 14 | 10.04.2022 | GV - 14 Date : 10.03.2022 |  | Yes
8 | Pressure Guage | 0 - 16 Kg/cm2 | GV - 08 | 10.04.2022 | GV - 08 Date : 10.03.2022 |  | Yes
9 | Pressure Guage | 0 - 16 Kg/cm2 | GV -16 | 20.03.2022 | GV - 16 Date : 20.02.2022 |  | Yes
10 | Pressure Guage | 0 - 16 Kg/cm2 | GV - 346 | 10.04.2022 | GV - 346 Date : 10.03.2022 |  | Yes
11 | Pressure Guage | 0 - 16 Kg/cm2 | GV - 345 | 10.04.2022 | GV - 345 Date : 10.03.2022 |  | Yes
12 | Pressure Guage | 0 - 16 Kg/cm2 | GV - 335 | 10.04.2022 | GV - 335 Date : 10.03.2022 |  | Yes
13 | Pressure Guage | 0 - 16 Kg/cm2 | GV - 332 | 10.04.2022 | GV - 332 Date : 10.03.2022 |  | Yes
14 | Pressure Guage | 0 - 16 Kg/cm2 | GV - 353 | 20.04.2022 | GV - 353 Date : 20.03.2022 |  | Yes
15 | Pressure Guage | 0 - 16 Kg/cm2 | GV - 348 | 20.04.2022 | GV - 348 Date : 20.03.2022 |  | Yes
16 | Pressure Guage | 0 - 16 Kg/cm2 | GV - 347 | 10.04.2022 | GV - 341 Date : 10.03.2022 |  | Yes
17 | Pressure Guage | 0 - 16 Kg/cm2 | GV - 01 | 10.04.2022 | GV - 01 Date : 10.03.2022 |  | Yes
18 | Pressure Guage | 0 - 16 Kg/cm2 | GV - 25 | 10.04.2022 | GV - 25 Date : 10.03.2022 |  | Yes
19 | Pressure Guage | 0 - 25 Kg/cm2 | GV - 366 | 10.04.2022 | GV - 366 Date : 10.03.2022 |  | Yes
20 | Pressure Guage | 0 - 16 Kg/cm2 | GV - 27 | 10.04.2022 | GV - 27 Date : 10.03.2022 |  | Yes
21 | Measuring Tape | 0 - 5 Mtrs. | MT-02 | 10.11.2022 | 2021/11/0309 Dated. 10.11.2021 |  | Yes

## Areas of concerns
Areas Of Concern
Nil

## Pending Activities
Pending Activities from this visit
Nil

## Conclusion
Note: Data filled in this sheet will not upload in TIIMES
Non Conformities raised / Discrepancies observed during Inspection (If Any, Mention TUV India NCR Number ):
Identification of Inspected Item(s):
Conclusion (Acceptable / Not Acceptable / Acceptance subject to):
IRN can be issued for PO Item numbers:
Expenses:
Remarks: