## Notes
Notes:
Data filled in General and conclusion Sections will not upload in TIIMES. Please use these sections to keep data ready for copy paste.
Data in Item Description columns of Accepted Quantity and cumulative Accepted quantity must be verified thoroughly before uploading in TIIMES.
Pending activity, Areas of concern & Details of measuring instruments sheets are applicable for IVR.
Select options from drop down list for unit of measurement (Item Description) & certifying body of measuring instruments (Details of measuring instruments).
Do not modify this format.
To start next row in cell itself use below shortcut: press 'alt + Enter' keys together. Alt + Enter

## General
Note: - Data filled in this sheet will not upload in TIIMES
Title | Details
Control Number
SAP number
Notification Number
Project Name & Location
Client Name
End User Name
DEC / PMC / EPC Name
DEC / PMC / EPC Number
Vendor Name
PO Number (Client PO on Vendor)
Sub Vendor
PO Number (Vendor PO on Sub Vendor)
Inspection Location
Inspection Date(s)

## Item Description
Po Item No. | Item Code | Item Description | Unit | Po Quantity | Offered Quantity | Accepted Quantity (Please verify thouroghly before using this Column for IRN) | Cumulative Accepted Quanitity (for IRN Only)
10 | 768-100-A01 | SEAMLESS PIPE ASTM A106 GRADE B EN 10204:2004 INSP. CERT. 3.2 TUV SIZE : 168.3 (6") OD X 7.11 (Sch STD) Thk X11186 mm long MOC : ASTM A 106 Gr B End : BEVEL Heat No : 3215814 - 63 nos.(704.72 Mtrs) & 3123864 - 287 Nos (3210.28 Mtrs.) MTC No : JSAW/Q/4111005243 Date : 18/09/2022. RMTC No : JS3/0000037523 Date : 04/05/2022 & JS3/0000036944 Date: 22.01.2022. | meter | 4698.12 | 3915.10 Mtr. (350 Nos.) | 3915.10 Mtr. (350 Nos.) | 3915.10 Mtr. (350 Nos.) | number
meter
km
meter (number)
km (number)
each
Piece
Test sample
AU - All Unit
lot
Set
Running Meter
kg
metric ton (tonne)
ton
cubic millimetre
cubic centimeter
cubic meter
cubic inch
cubic foot
mm
cm
in
foot
mile
yard
liter
kl
cl
ml
g
lb
oz
Sq. mm
Sq. cm
Sq. meter
Sq. in
Sq. foot

## Reference Documents
Sr. No. | Document Name | Client Document Number | Vendor Document Number | Approval Status
1 | PR/MR/ARM | Not Applicable | Not Applicable | Not Applicable
2 | QAP/ITP/QCP | Not Applicable | ITP/2022/DUKL/6715000470-1 Rev-01 | Approved by PAUL.HILLYARD Dated : 25.07.2022
3 | Drawing(s) | Not Applicable | Not Applicable | Not Applicable
4 | Procedure(s) | Not Applicable | Not Applicable | Not Applicable
5 | Datasheet(s) | Not Applicable | Not Applicable | Not Applicable
6 | Others (Specify) | ASTM A 106 & PO ordering notes | Not Applicable | ASTM Std. & client Requirements

## Stages Witnessed
Stages Witnessed
As Per ITP Sr. No - 03 : Mechanical Test a) One Number of Pipe sample, per size per heat stamped for Mechanical test (Tensile & flattening) witness at Lab. b) Tensile test of identified sample witnessed – obtained value of UTS, % Elongation & yield stress confirms the required material grade specification. c) Flattening test of pipe sample witnessed – Test found satisfactory.
As Per ITP Sr. No - 04 : Chemical Test (Product analysis) a) One Number of Pipe sample, per size per heat stamped for Chemical test witness at Lab. b) chemical test of identified sample witnessed – obtained element % confirms the required material grade specification.
As Per ITP Sr. No - 04 : Hydrostatic Pressure Test / Leak Test Tightness Test : a) Hydrostatic test for randomly selected 10% of pipe of each size from offered quantity witnessed at a test pressure of 2800 PSI & pressure holding time of 05 sec. minimum – No leakage / No Pressure Drop observed - Test found satisfactory. b) Pipes are in varnished condition (outer surface) during hydrostatic test.
As Per ITP Sr. No - 05 : Visual Inspection. a) Visual Inspection of randomly selected 10% of pipe for each size checked (for outer surface & up to visible area for pipe inside), no pitting, dent, lamination, surface discontinuities, and injurious defects are observed at the time of inspection - visual inspection found satisfactory. b) Varnishing on outer surface of pipe observed during visual inspection.
As Per ITP Sr. No - 06 : Dimensional Inspection a) Dimensional Inspection for randomly selected 10% of pipe of each size from offered quantity witnessed. b) Dimensions for OD, Thickness (at pipe end & along the length at random), Bevel angle, root face, total length of pipe, Ovality checked – found within tolerance as per standard and QAP/PO requirements.
As Per ITP Sr. No - 07 : Pipe Marking a) Pipe Marking verified – details about Supplier Logo, MOC of Pipe, Manufacturing process (CDS/HFS), Pipe Size, Wight per meter, Hydro test pressure, Heat No. , BIH No, bundle No. found on pipe marking - as mentioned in approved QAP & PO.
Witness Pipe Details are A) SIZE : 168.3 (6") OD X 7.11 (Sch STD) Thk X11186 mm long MOC : ASTM A 106 Gr B End : BEVEL Heat No : 3215814 Bundle No. FLIH01065 (07 Nos), FLIAPI0290 (07 Nos) & FLIAPI0291 (04 Nos) B) SIZE : 168.3 (6") OD X 7.11 (Sch STD) Thk X11186 mm long MOC : ASTM A 106 Gr B End : BEVEL Heat No : 3123864 Bundle No. FLIAPI0249 (07 Nos), FLIAPI0251 (07 Nos), FLIAPI0274 (07 Nos).

## Document reviewed
Document reviewed
As per ITP Sr. No. 01 Round Billet Test certificate (RMTC) reviewed - found in order.
Manufacturer’s Internal report for Hydrostatic test, Visual & Dimensional Inspection reviewed – found in order.
Manufacturer test certificate in EN10204 3.2 reviewed - found to meet specification /PO requirement.
Calibration test certificate of Instrument used for inspection reviewed, Found in order.

## Details of measuring instrument
Sr. No. | Detail of Equipment(s) / Instrument(s) | Range | ID | Validity till Date | Calibration Certificate Number | NABL / OTHER CERT. BODIES / NABL Traceability (type Yes wherever applicable) | NON-NABL (type Yes wherever applicable)
1 | Pressure Gauge | 0 - 420 Kg/cm2 | PG-420/N293. 59-01626 | 07.10.2022 | JSAW/PG/420/34 Date : 08.09.2022 |  | Yes | Yes
2 | Pressure Recorder | 0 - 30000 PSI | HYD-04 | 2022-10-23 | ET.2022/06/66/004 Date : 24.06.2022 | Yes |  | No
3 | Bevel Protractor | 0 Deg-90 Deg.-0 Deg | BP-05 | 21.12.2022 | ME.2021/12/64/005 Date : 22.12.2021 | Yes
4 | Micro meter | 0 - 25 mm | TM25/73 | 21.10.2022 | JSL-265 A Date : 22.04.2022 |  | Yes
5 | Vernier Calliper | 0 - 300 mm | VC 300/28 | 06.07.2023 | JSL-352 Date : 07.07.2022 |  | Yes
6 | Universal Testing Machine | 0 - 1000 KN | JSAW/UTM/01 | 11.08.2023 | SME/22/1625 Date : 12.08.2022 | Yes
7 | Slip Gauge Set | 0.5-100 mm | SG-01 | 08.10.2023 | 2021/10/1467 Date : 11.10.2021 | Yes
8 | Measuring Tape | 0 - 15 Mtr | JSL-MT-01 | 19.11.2022 | ME.2022/05/02/003 Date : 19.11.2022 | Yes

## Areas of concerns
Areas Of Concern
None

## Pending Activities
Pending Activities from this visit
None

## Conclusion
Note: Data filled in this sheet will not upload in TIIMES
Non Conformities raised / Discrepancies observed during Inspection (If Any, Mention TUV India NCR Number ):
Identification of Inspected Item(s):
Conclusion (Acceptable / Not Acceptable / Acceptance subject to):
IRN can be issued for PO Item numbers:
Expenses:
Remarks: