## Notes
Notes:
Data filled in General and conclusion Sections will not upload in TIIMES. Please use these sections to keep data ready for copy paste.
Data in Item Description columns of Accepted Quantity and cumulative Accepted quantity must be verified thoroughly before uploading in TIIMES.
Pending activity, Areas of concern & Details of measuring instruments sheets are applicable for IVR.
Select options from drop down list for unit of measurement (Item Description) & certifying body of measuring instruments (Details of measuring instruments).
Do not modify this format.
To start next row in cell itself use below shortcut: press 'alt + Enter' keys together. Alt + Enter

## General
Note: - Data filled in this sheet will not upload in TIIMES
Title | Details
Control Number
SAP number
Notification Number
Project Name & Location
Client Name
End User Name
DEC / PMC / EPC Name
DEC / PMC / EPC Number
Vendor Name
PO Number (Client PO on Vendor)
Sub Vendor
PO Number (Vendor PO on Sub Vendor)
Inspection Location
Inspection Date(s)

## Item Description
Po Item No. | Item Code | Item Description | Unit | Po Quantity | Offered Quantity | Accepted Quantity (Please verify thouroghly before using this Column for IRN) | Cumulative Accepted Quanitity (for IRN Only)
3 | 9002713 | Description: VALVE BALL MS-PTFE FE ASA150# 3", V-871 GENERAL : VALVE TYPE : PFA LINED BALL VALVE (FULL PORT) RATING : ASA 150# END CONNECTION | number | 30 | 30 | 30 | 30 | number
4 | 9606238 | Description: VALVE BALL MS-PTFE FE ASA150# 6", V-871 GENERAL : VALVE TYPE : PFA LINED BALL VALVE (FULL PORT) RATING : ASA 150# END CONNECTION | number | 6 | 6 | 6 | 6 | meter
km
meter (number)
km (number)
each
Piece
Test sample
AU - All Unit
lot
Set
Running Meter
kg
metric ton (tonne)
ton
cubic millimetre
cubic centimeter
cubic meter
cubic inch
cubic foot
mm
cm
in
foot
mile
yard
liter
kl
cl
ml
g
lb
oz
Sq. mm
Sq. cm
Sq. meter
Sq. in
Sq. foot

## Reference Documents
Sr. No. | Document Name | Client Document Number | Vendor Document Number | Approval Status
1 | PR/MR/ARM | Not Applicable | Not Applicable | Not Applicable
2 | QAP/ITP/QCP | Not Applicable | QAP NO:12_22_01 , REV:00 (INSPECTION & TEST PLAN FOR PFA LINED BALL VALVES) Dated: 14.12.2022 | Approved by client vide e­mail dated 15.12.2022.
3 | Drawing(s) | Not Applicable | 22-23/SSC-420, REV:00 Dated 28.11.2022 (6") & 22-23/SSC-421, REV:00 Dated 28.11.2022 (3") | Approved by client vide e­mail dated 15.12.2022.
4 | Procedure(s) | Not Applicable | Not Applicable | Not Applicable
5 | Datasheet(s) | Not Applicable | Not Applicable | Not Applicable
6 | Others (Specify) | Not Applicable | Not Applicable | Not Applicable

## Stages Witnessed
Stages Witnessed
QAP Sr No 1 ; Dimension checked 100% of valves offered lot ­ found satisfactory as per the drawing requirements.
QAP Sr No 2 ; Size - 3" x 150 #- Hydrostatic test of seat and body witnessed 100% of valves offered lot at 12 Kg/cm2(g) { Required Pressure : 10 Kg/cm2 } and 17 Kg/cm2(g) { Required Pressure : 15Kg/cm } respectively with holding time of 3 minutes minimum for each test ­ no leakage or pressure drop was observed during the required holding period.
QAP Sr No 2 ; Size - 6" x 150 #- Hydrostatic test of seat and body witnessed 100% of valves offered lot at 08 Kg/cm2(g) { Required Pressure :07 Kg/cm2 } and 15 Kg/cm2(g) { Required Pressure : 14 Kg/cm2 } respectively with holding time of 3 minutes minimum for each test ­ no leakage or pressure drop was observed during the required holding period.
QAP Sr No 3 ; Spark test of lining witnessed at 15 KVDC 100% of valves offered lot ­ found satisfactory without any spark
QAP Sr No 4 ; Visual checked 100% of valves offered lot with painted condition ­ found satisfactory except that in most of the valves the paint has been found damaged at random location which needs to be rectified. Also in all the valves, the painting needs to be carried out in the bolt holes which have been left unpainted - As per mail gvien by Client Dated 29.11.2022 same to be follow fo paint final visual inspection wavier and vendor to be done as per client requirement
Marking Verifed - found in order.
All measuring instruments/ equipment were verified for continued suitability for intended use, proper identification, calibration status, traceability to national standards & found satisfactory.

## Document reviewed
Document reviewed
QAP Sr No 1, 2, 3 & 4 ; Raw Material test certificate reviewed declared by Supplier - Found to meet the specification requirements.
Verified calibration certification of all used instruments for inspection – Found in order.

## Details of measuring instrument
Sr. No. | Detail of Equipment(s) / Instrument(s) | Range | ID | Validity till Date | Calibration Certificate Number | NABL / OTHER CERT. BODIES / NABL Traceability (type Yes wherever applicable) | NON-NABL (type Yes wherever applicable)
1 | Pressure Gauge | 0 - 42 Kg/cm2 | 13138649168 | 11.03.2023 | PG ­ 6993 Dtd : 12.03.2022 | Yes | No | Yes
2 | Vernier Caliper | 0 ­ 300 mm | 13056068 | 16.01.2023 | KS/CC/D­0764 Dtd : 17.01.2023 |  | Yes | No
3 | Spark Tester | 0 ­ 40 KV | 848 | 03.01.2023 | AE/21­22/300 Dtd : 04.01.2022 |  | Yes

## Areas of concerns
Areas Of Concern
1.- Size : 25 NB and 40 NB - ONLY FOR INFORMATION PURPOSE The handle of the valves is towards one side as against that shown in the drawing - As per mail gvien by Client mail Dated 29.11.2022 same to be follow - for infomration only
3. - In most of the valves the paint has been found damaged at random location which needs to be rectified. Also in all the valves, the painting needs to be carried out in the bolt holes which have been left unpainted - As per mail gvien by Client Dated 29.11.2022 same to be follow fo paint final visual inspection wavier and vendor to be done as per client requirement

## Pending Activities
Pending Activities from this visit

## Conclusion
Note: Data filled in this sheet will not upload in TIIMES
Non Conformities raised / Discrepancies observed during Inspection (If Any, Mention TUV India NCR Number ):
Nil
Identification of Inspected Item(s):
Conclusion (Acceptable / Not Acceptable / Acceptance subject to):
IRN can be issued for PO Item numbers:
Expenses:
Remarks: