## Notes
Notes:
Data filled in General and conclusion Sections will not upload in TIIMES. Please use these sections to keep data ready for copy paste.
Data in Item Description columns of Accepted Quantity and cumulative Accepted quantity must be verified thoroughly before uploading in TIIMES.
Pending activity, Areas of concern & Details of measuring instruments sheets are applicable for IVR.
Select options from drop down list for unit of measurement (Item Description) & certifying body of measuring instruments (Details of measuring instruments).
Do not modify this format.
To start next row in cell itself use below shortcut: press 'alt + Enter' keys together. Alt + Enter

## General
Note: - Data filled in this sheet will not upload in TIIMES
Title | Details
Control Number
SAP number
Notification Number
Project Name & Location
Client Name
End User Name
DEC / PMC / EPC Name
DEC / PMC / EPC Number
Vendor Name
PO Number (Client PO on Vendor)
Sub Vendor
PO Number (Vendor PO on Sub Vendor)
Inspection Location
Inspection Date(s)

## Item Description
Po Item No. | Item Code | Item Description | Unit | Po Quantity | Offered Quantity | Accepted Quantity (Please verify thouroghly before using this Column for IRN) | Cumulative Accepted Quanitity (for IRN Only)
210 |  | STATIONARY HEAD FLG.: 1562 OD X 926.8 MM ID X 293.6 MM THK AS PER SKETCH NO.SK-6020 REV.1 | number | 4 | 1 | 1 | 4 | number
meter
km
meter (number)
km (number)
each
Piece
Test sample
AU - All Unit
lot
Set
Running Meter
kg
metric ton (tonne)
ton
cubic millimetre
cubic centimeter
cubic meter
cubic inch
cubic foot
mm
cm
in
foot
mile
yard
liter
kl
cl
ml
g
lb
oz
Sq. mm
Sq. cm
Sq. meter
Sq. in
Sq. foot

## Reference Documents
Sr. No. | Document Name | Client Document Number | Vendor Document Number | Approval Status
1 | PR/MR/ARM
2 | QAP/ITP/QCP |  | CHW/QAP/E495-3 Rev.1 Date: 25.02.21 | Approved by Anup Engineering
3 | Drawing(s) | As mentioned in Item description |  | Approved by Anup Engineering
4 | Procedure(s)
5 | Datasheet(s) | H-2477-88-SA182F6ACL2-FORG Rev.0 Date: 23.07.20 |  | Approved by Anup Engineering
6 | Others (Specify)

## Stages Witnessed
Stages Witnessed
QAP Sr. No.5-Selection and stamping of test samples.
QAP Sl. No.6-Witnessed Mechanical test (Tensile, Impact & Hardness) & Product Analysis, found acceptable as per TPS and material specification.
QAP Sr. No.7-Witnessed Ultrasonic test @100% as per Article 23 & SA388 of ASME Sec. V, ED.2019, with acceptance criteria as per Paragraph 3.3.4 of ASME Sec. VIII Div.2, ED.2019, found acceptable.
QAP Sr. No.7-Witnessed Liquid Penetrant Examination @100% as per Article 6 of ASME Sec. V, ED.2019, with acceptance criteria as per Appendix 8 of ASME Sec. VIII Div.1, ED.2019 and found acceptable.
QAP Sr. No.8-Witnessed PMI @100% as per 6-81-0001, with acceptance criteria as per material specification and found acceptable.
QAP Sl. No.9 & 10-Witnessed Visual, Dimension as per PO & Marking @100% as per PO & TPS requirements, found acceptable.

## Document reviewed
Document reviewed
QAP Sr. No.2 & 4-Raw material certificate and Heat treatment chart verified as per PO, Client's specification and material specification requirement, found acceptable.
QAP Sl. No.11-Reviewed and endorsed manufacturer's MTC No. CHW/QC/21-22/2109 Date : 18-10-21

## Details of measuring instrument
Sr. No. | Detail of Equipment(s) / Instrument(s) | Range | ID | Validity till Date | Calibration Certificate Number | NABL / OTHER CERT. BODIES / NABL Traceability (type Yes wherever applicable) | NON-NABL (type Yes wherever applicable)
1 | Vernier Calliper | 0-300 MM | 1144458 | 30.12.21 | PMM/DVC/10976/1, 02.01.21 | Yes |  | Yes
2 | Vernier Calliper | 0-2000 MM | 534 | 22.12.21 | PMM/DVC/10908/1, 24.12.20 | Yes |  | No
3 | Alloy Analyser |  | 583043 | 21.11.21 | IR TECH/AC/AMF/22/2021-22, 22.05.21 |  | Yes
4 | Ultrasonic Machine |  | E4575-0316 | 18.12.21 | MIMCO/UFD/E4575/2020-21, 19.12.20 |  | Yes

## Areas of concerns
Areas Of Concern

## Pending Activities
Pending Activities from this visit

## Conclusion
Note: Data filled in this sheet will not upload in TIIMES
Non Conformities raised / Discrepancies observed during Inspection (If Any, Mention TUV India NCR Number ):
Identification of Inspected Item(s):
Conclusion (Acceptable / Not Acceptable / Acceptance subject to):
IRN can be issued for PO Item numbers:
Expenses:
Remarks: