## Notes
Notes:
Data filled in General and conclusion Sections will not upload in TIIMES. Please use these sections to keep data ready for copy paste.
Data in Item Description columns of Accepted Quantity and cumulative Accepted quantity must be verified thoroughly before uploading in TIIMES.
Pending activity, Areas of concern & Details of measuring instruments sheets are applicable for IVR.
Select options from drop down list for unit of measurement (Item Description) & certifying body of measuring instruments (Details of measuring instruments).
Do not modify this format.
To start next row in cell itself use below shortcut: press 'alt + Enter' keys together. Alt + Enter

## General
Note: - Data filled in this sheet will not upload in TIIMES
Title | Details
Control Number
SAP number
Notification Number
Project Name & Location
Client Name
End User Name
DEC / PMC / EPC Name
DEC / PMC / EPC Number
Vendor Name
PO Number (Client PO on Vendor)
Sub Vendor
PO Number (Vendor PO on Sub Vendor)
Inspection Location
Inspection Date(s)

## Item Description
Po Item No. | Item Code | Item Description | Unit | Po Quantity | Offered Quantity | Accepted Quantity (Please verify thouroghly before using this Column for IRN) | Cumulative Accepted Quanitity (for IRN Only)
1 | 2002210633 | Parts for Exchanger ion Tube Bundle, W/Channel intergral(Reactor Effluent HP Steam Generator) Tag No.: MERH362S36 Mfg. Sr. No.: H2600 | each | 1 | 1 | 1 | 1 | number
meter
km
meter (number)
km (number)
each
Piece
Test sample
AU - All Unit
lot
Set
Running Meter
kg
metric ton (tonne)
ton
cubic millimetre
cubic centimeter
cubic meter
cubic inch
cubic foot
mm
cm
in
foot
mile
yard
liter
kl
cl
ml
g
lb
oz
Sq. mm
Sq. cm
Sq. meter
Sq. in
Sq. foot

## Reference Documents
Sr. No. | Document Name | Client Document Number | Vendor Document Number | Approval Status
1 | PR/MR/ARM | Not Applicable | Not Applicable | Not Applicable
2 | QAP/ITP/QCP | 22960-MMH-240380419-362-A05-001Rev.01 | AEL/ITP/H2600 Rev.01Dated20.10.2021 | Approved in Code -1 By RIL
3 | Drawing(s) | 22960-MMH-240380419-362-F01-001-02 22960-MMH-240380419-362-F01-002-02 22960-MMH-240380419-362-F01-003-00 | H-2600-FAD-2021 SH. 1 OF 2 REV.02 H-2600-FAD-2021 SH. 2 OF 2 REV.02 H-2600-TRANS-2021, Rev.00 sheet 1 Of 1 | Approved in Code -1 By RIL
4 | Procedure(s) | NDE Procedure: 22960-MMH-240380419-362-J02-001, Rev.00 Hydro Test Procedure: 22960-MMH-240380419-362-K02-001, Rev.00 Heat Treatment Procedure: 22960-MMH-240380419-362-J03-001, Rev.01 Surface Preparation, Painting & Coating Procedure: 22960-MMH-240380419-362-J04-001, Rev.01 | AEL/NDE/H-2600, Rev.00 AEL/HYDRO/H-2600, Rev.00 AEL/HT/H-2600, Rev.01 AEL/PAINTING/H-2600, Rev.01 | Approved in Code -1 By RIL
5 | Datasheet(s) | Not Applicable | Not Applicable | Not Applicable
6 | Others (Specify) | Not Applicable | Not Applicable | Not Applicable

## Stages Witnessed
Stages Witnessed
ITP Stage no. 1.4 Witnessed Mock up test for tube to tube sheet joint as per approved ITP requirements - Found acceptable.
ITP stage no. 3.1, 3.3 & 3.5 Witnessed Material identification of pressure parts & bought out items as per ITP requirements-Found acceptable.
ITP stage no. 3.1, 3.3 & 3.5 Witnessed Material identification of pressure parts (plates and pipes) & bought out items (forgings, tubes) as per ITP requirements-Found acceptable.
ITP Stage no.6.1 Visual & Dimension inspection carried out of Tube sheet after machining & drilling as per drawing - Found acceptable.
ITP stage no.6.4 Witnessed PMI Examination carried out for Tube Bundle Assembly - Found acceptable.
ITP Stage no.6.5 Witnessed PT Examination carried out for Final weld of Tube to Tube sheet joints - No relevant indication observed found acceptable.
ITP Stage no.6.6 Witnessed Pneumatic test for Tube to Tube sheet Joint at pressure 1.05 kg/cm2(g) after Final weld, checked with soap solution - neither leakage nor bubble formation observed during testing.
ITP Stage no.6.7 Random Witnessed expansion check for tube to tube sheet joint after expansion - Found acceptable.
ITP Stage no.6.9 Witnessed Dimension and Visual inspection carried out for complete Tube Bundle Assembly including Tube to Tube sheet joint as per drawing - Found acceptable
ITP Stage no.7.1 Visual & Dimension inspection carried out of Channel Shell Assembly before PWHT with pass partition plate and before fitup with Tube sheet as per drawing - Found acceptable.
ITP Stage no.7.3 Witnessed Circumference fitup inspection carried out of Channel Shell Assembly with Tube sheet as per drawing - Found acceptable.
ITP Stage no.7.5 Visual & Dimension inspection carried out of complete Channel Shell Assembly with Tube sheet after PWHT as per drawing - Found acceptable.
ITP Stage no.7.6 Random Witnessed Hardness check on Weld, HAZ and parent metal from outside and Weld overlay from inside after PWHT- Found acceptable.
ITP Stage no.7.7 Witnessed Pneumatic test for R.pad final weld joints of Nozzles at pressure 1.05 kg/cm2(g) after PWHT, checked with soap solution - neither leakage nor bubble formation observed during testing, Acceptable.
ITP Stage no.7.8 Random witnessed of PMI Examination carried out for Welded joints, Low alloy steel parts from outside and Clad plate, Weld overlay from inside - Found acceptable.
ITP Stage no: 8.1 Witnessed for Open Bundle - tube side Hydrostatic test at a pressure of 123 Kg/cm2g holding for 60 minutes minimum in horizontal position - Found no leakage no pressure drop during the test and no any deformation found during the test, Acceptable.
ITP Stage no: 8.2 Witnessed for Shell side Hydrostatic test(with tube bundle inserted in dummy shell without channel cover ) at a pressure of 82.5 Kg/cm2g holding for 60 minutes minimum in horizontal position - Found no leakage no pressure drop during the test and no any deformation found during the test, Acceptable.
ITP stage no.9.1 Witnessed Draning and Drying of equipment at Shell side and Tube side after Hydrotest, no water particles observed. Equipment completely dried - Found satisfactory.
ITP stage no.9.2 Visual inspection, CuSO4 & Litmus paper test carried out on inside surface for Channel Shell Assembly and Tube sheet after pickling and passivation - Found acceptable.
ITP stage no. 9.4 - Visual inspection carried out for external surface of Channel Shell Assembly after Painting - Found Satisfactory. - Checked DFT on External surface of Channel Shell Assembly - DFT found as per Painting procedure requirements, Acceptable. - Adhesion test carried out as per Painting procedure requirements - Acceptable.
ITP stage no. 9.5 Verified Rub-off details - Found acceptable.
ITP Stage no. 9.7 - Witnessed N2 purging at pressure 1.3 kg/cm2 (g) in Exhaust nozzle of Shell side & Tube side. Verified bolting Joints with soap solution - Neither leakage nor bubble formation observed. - Found acceptable.
All measuring instruments/ equipment were verified for continued suitability for intended use, proper identification, calibration status, traceability to national standards & found satisfactory

## Document reviewed
Document reviewed
ITP stage no: 1.3 Reviewed WPS/PQR along with weld map - Found in order.
ITP stage no: 1.5 Reviewed welder certificate & NDE Personnel qualification certificate - Found in order.
ITP stage no: 3.1 to 3.5 Reviewed Material heat chart for pressure parts, Direct attached to pressure parts along with Material test certificate - Found to meet material specification requirements.
ITP stage no: 3.6 Reviewed Material heat chart for Non-pressure parts along with Material test certificate - Found to meet material specification requirements.
ITP stage no: 4.1 Reviewed Longseam fitup inspection reports of Channel shell and Fab.pipe - Found in order.
ITP stage no: 4.2 Reviewed Circumference fitup inspection reports of Channel shell to Girth flange weld joint - Found in order.
ITP stage no: 4.3 Reviewed Circumference fitup inspection reports of Fab.pipe to Flange weld joint for Nozzles - Found in order.
ITP stage no: 4.4 Reviewed Nozzle cut-out opening marking inspection reports - Found in order.
ITP stage no: 4.5 Reviewed Nozzle fitup inspection reports - Found in order.
ITP stage no: 4.6 Reviewed Internal and External attachments fitup inspection reports - Found in order.
ITP stage no: 5.1 Reviewed weld consumable test certificate - Found in order.
ITP stage no: 5.4 Reviewed PT Examination report of each layer of weld overlay as per ITP requirements-Found in order.
ITP stage no: 5.5 Reviewed Weld overlay chips wet chemical analysis lab check test reports as per ITP requirements-Found in order.
ITP stage no: 5.6 Reviewed PT Examination report for WEP, Back chip and Root run of weld joints per ITP requirements-Found in order.
ITP stage no: 5.7 - Reviewed PT Examination reports as per ITP requirements-Found in order. - Reviewed RT films for butt weld Joints & RT Summary -Found acceptable.
ITP Stage no: 6.2 Reviewed Baffle inspection report-Found in order.
ITP stage no: 6.3 Reviewed Tube bundle skeleton visual and dimension inspection report before Tube insertion-Found in order
ITP stage no: 6.5 Reviewed PT Examination reports of Tube to Tube sheet weld joint after Root run welding as per ITP requirement-Found in order.
ITP stage no: 6.8 Reviewed Heat Treatment Chart of Tube to Tube sheet weld joint as per ITP, Drawing and Heat Treatment procedure requirement-Found in order.
ITP stage no: 7.2 Reviewed Heat Treatment Chart of Channel Shell Assembly as per ITP, Drawing and Heat Treatment procedure requirement-Found in order.
ITP stage no: 7.4 Reviewed Heat Treatment Chart of Channel Shell Assembly to Tube sheet weld joint as per ITP, Drawing and Heat Treatment procedure requirement-Found in order.
ITP stage no: 9.3 Reviewed Surface preparation & painting inspection report-Found in order.
ITP Stage no: 9.8 Reviewed all documents as per approved ITP requirements-found in order.

## Details of measuring instrument
Sr. No. | Detail of Equipment(s) / Instrument(s) | Range | ID | Validity till Date | Calibration Certificate Number | NABL / OTHER CERT. BODIES / NABL Traceability (type Yes wherever applicable) | NON-NABL (type Yes wherever applicable)
1 | Ultrasonic thickness gauge | 2.0 to 200mm | UTG-02 | 24.12.2022 | Paramount/64200 Dated 25.12.2021 |  | Yes | Yes
2 | Measuring Tape | 0-5000 mm | MT-10 | 28.12.2022 | Paramount/64279 Dated 29.12.2021 |  | Yes | No
3 | Measuring Tape | 0-15000 mm | MT-21 | 28.12.2022 | Paramount/64290 Dated 29.12.2021 |  | Yes
4 | Vernier calliper | 0-300 mm | LVC 0402 | 30.08.2022 | Paramount/60825 dated 31.08.2021 |  | Yes
5 | Pressure gauge | 0 to 300 Kg/cm2 | APG/300/02 | 06.09.2022 | AEL/2022/71 DT : 07.03.2022 |  | Yes
6 | Pressure gauge | 0 to 300 Kg/cm2 | APG/300/03 | 06.09.2022 | AEL/2022/71 DT : 07.03.2022 |  | Yes

## Areas of concerns
Areas Of Concern

## Pending Activities
Pending Activities from this visit
none

## Conclusion
Note: Data filled in this sheet will not upload in TIIMES
Non Conformities raised / Discrepancies observed during Inspection (If Any, Mention TUV India NCR Number ):
Identification of Inspected Item(s):
Conclusion (Acceptable / Not Acceptable / Acceptance subject to):
IRN can be issued for PO Item numbers:
Expenses:
Remarks: