## Notes
Notes:
Data filled in General and conclusion Sections will not upload in TIIMES. Please use these sections to keep data ready for copy paste.
Data in Item Description columns of Accepted Quantity and cumulative Accepted quantity must be verified thoroughly before uploading in TIIMES.
Pending activity, Areas of concern & Details of measuring instruments sheets are applicable for IVR.
Select options from drop down list for unit of measurement (Item Description) & certifying body of measuring instruments (Details of measuring instruments).
Do not modify this format.
To start next row in cell itself use below shortcut: press 'alt + Enter' keys together. Alt + Enter

## General
Note: - Data filled in this sheet will not upload in TIIMES
Title | Details
Control Number
SAP number
Notification Number
Project Name & Location
Client Name
End User Name
DEC / PMC / EPC Name
DEC / PMC / EPC Number
Vendor Name
PO Number (Client PO on Vendor)
Sub Vendor
PO Number (Vendor PO on Sub Vendor)
Inspection Location
Inspection Date(s)

## Item Description
Po Item No. | Item Code | Item Description | Unit | Po Quantity | Offered Quantity | Accepted Quantity (Please verify thouroghly before using this Column for IRN) | Cumulative Accepted Quanitity (for IRN Only)
|  | Spare Pipe | [5 empty] | number
2 |  | Heater Tag No. 86-F-01A/01B Radiant Outlet Coils 114.3 OD, 8.56 AWT (Bare Tubes) Lenght: 5990mm Material: A335 Gr. P9 | number | 1 | 1 | 1 | 1 | meter
5 |  | Heater Tag No. 86-F-01A/01B Radiant Outlet Coils 114.3 OD, 8.56 AWT (Bare Tubes) Lenght: 6000mm Material: A335 Gr. P9 | number | 1 | 1 | 1 | 1 | km
6 |  | Heater Tag No. 86-F-01A/01B Convection Outlet Coil 101.6 OD ,8.08 AWT (Bare Tubes) Lenght: 5974mm Material: A335 Gr. P9 | number | 1 | 1 | 1 | 1 | meter (number)
7 |  | Heater Tag No. 86-F-01A/01B Convection Outlet Coil 101.6 OD ,8.08 AWT (Bare Tubes) Lenght: 11000mm Material: A335 Gr. P9 | number | 4 | 4 | 4 | 4 | km (number)
7 |  | Heater Tag No. 86-F-01A/01B Convection Outlet Coil 101.6 OD ,8.08 AWT (Bare Tubes) Lenght: 11958mm Material: A335 Gr. P9 | number | 2 | 2 | 2 | 2 | each
8 |  | Heater Tag No. 86-F-01A/01B Convection Outlet Coil 101.6 OD ,8.08 AWT (Bare Tubes) Lenght: 9580mm Material: A335 Gr. P9 | number | 1 | 1 | 1 | 1 | Piece
10 |  | Heater Tag No. 86-F-01A/01B Convection Outlet Coil 101.6 OD ,8.08 AWT (Studded Tubes) Lenght: 5980mm Material: A335 Gr. P9 | number | 8 | 8 | 8 | 8 | Test sample
11 |  | Heater Tag No. 86-F-01A/01B Convection HP SSH Inlet Coils 114.3 OD, 7.49 AWT (Bare Tubes) Lenght: 11960mm Material: SA213 Gr. T11 | number | 1 | 1 | 1 | 1 | AU - All Unit
11 |  | Heater Tag No. 86-F-01A/01B Convection HP SSH Inlet Coils 114.3 OD, 7.49 AWT (Bare Tubes) Lenght: 5974mm Material: SA213 Gr. T11 | number | 1 | 1 | 1 | 1 | lot
12 |  | Heater Tag No. 86-F-01A/01B Convection HP SSH Process Coils 114.3 OD, 7.49 AWT (Bare Tubes) Lenght: 11000mm Material: SA213 Gr. T11 | number | 2 | 2 | 2 | 2 | Set
12 |  | Heater Tag No. 86-F-01A/01B Convection HP SSH Process Coils 114.3 OD, 7.49 AWT (Bare Tubes) Lenght: 11960mm Material: SA213 Gr. T11 | number | 1 | 1 | 1 | 1 | Running Meter
13 |  | Heater Tag No. 86-F-01A/01B Convection LP SSH Outlet Coils 114.3 OD, 5.27 AWT (Bare Tubes) Lenght: 11960mm Material: SA213 Gr. T11 | number | 1 | 1 | 1 | 1 | kg
13 |  | Heater Tag No. 86-F-01A/01B Convection LP SSH Outlet Coils 114.3 OD, 5.27 AWT (Bare Tubes) Lenght: 5974mm Material: SA213 Gr. T11 | number | 1 | 1 | 1 | 1 | metric ton (tonne)
14 |  | Heater Tag No. 86-F-01A/01B Convection LP SSH Process Coils 114.3 OD, 5.27 AWT (Bare Tubes) Lenght: 11000mm Material: SA213 Gr. T11 | number | 2 | 2 | 2 | 2 | ton
14 |  | Heater Tag No. 86-F-01A/01B Convection LP SSH Process Coils 114.3 OD, 5.27 AWT (Bare Tubes) Lenght: 11960mm Material: SA213 Gr. T11 | number | 1 | 1 | 1 | 1 | cubic millimetre
15 |  | Heater Tag No. 86-F-01A/01B Convection HP SSH Inlet Manifold 168.3 OD, 9.27 AWT Lenght: 2306mm Material: A335 Gr. P9 | number | 1 | 1 | 1 | 1 | cubic centimeter
16 |  | Heater Tag No. 86-F-01A/01B Convection HP SSH Inlet Manifold 168.3 OD, 9.27 AWT Lenght: 2332mm Material: A335 Gr. P9 | number | 1 | 1 | 1 | 1 | cubic meter
cubic inch
cubic foot
mm
cm
in
foot
mile
yard
liter
kl
cl
ml
g
lb
oz
Sq. mm
Sq. cm
Sq. meter
Sq. in
Sq. foot

## Reference Documents
Sr. No. | Document Name | Client Document Number | Vendor Document Number | Approval Status
1 | PR/MR/ARM | N/A | N/A | N/A
2 | QAP/ITP/QCP | Scope of Inspection As per mail Given By HPIP on Dt.02.06.2023 | N/A | Scope of Inspection As per mail Given By HPIP on Dt.10.08.2023
3 | Drawing(s) | N/A | N/A | N/A
4 | Procedure(s) | N/A | N/A | N/A
5 | Datasheet(s) | N/A | N/A | N/A
6 | Others (Specify) | N/A | N/A | N/A

## Stages Witnessed
Stages Witnessed
Raw material identification Pipe – Found to meet the approved drawing, applicable code & project specification requirements.
Weld Visual inspection after completion of all fabrication activities from outside - No injurious surface imperfections were observed.
Penetrant test on final weld - No surface indication were observed.
PMI Inspection on Butt weld joint & parent metal – Found to meet the respective Material specification requirements.
Major dimensional inspection of Pipes - Found to meet the drawing requirement.
Hydro test witnessed at a pressure of 128 Kg/Cm² (g) (Required 126 Kg/Cm² (g) for Po Line Item 6,7,7,8,10 & 55 Kg/Cm² (g) (Required 126 Kg/Cm² (g) for Po Line 11,11,12,12 & 11 Kg/Cm² (g) (Required 10.50 Kg/Cm² (g) for Po Line Item 13,13,14,14 one hour holding period - No leakage or pressure drop observed during holding period.

## Document reviewed
Document reviewed
Raw material test certificates of pipe as declared by manufacturer endorsed by HPIP – Found to meet the respective material specification, code and project specification requirement.
Welding consumables batch test certificates - Found to meet the code requirement.
HT Chart Review – Found to meet the meet the applicable code specification requirement.
Radiography films of pipe to pipe joint after Stabilization - No significant indication were observed.

## Details of measuring instrument
Sr. No. | Detail of Equipment(s) / Instrument(s) | Range | ID | Validity till Date | Calibration Certificate Number | NABL / OTHER CERT. BODIES / NABL Traceability (type Yes wherever applicable) | NON-NABL (type Yes wherever applicable)
Yes
No

## Areas of concerns
Areas Of Concern

## Pending Activities
Pending Activities from this visit

## Conclusion
Note: Data filled in this sheet will not upload in TIIMES
Non Conformities raised / Discrepancies observed during Inspection (If Any, Mention TUV India NCR Number ):
Identification of Inspected Item(s):
Conclusion (Acceptable / Not Acceptable / Acceptance subject to):
IRN can be issued for PO Item numbers:
Expenses:
Remarks: