## Notes
Notes:
Data filled in General and conclusion Sections will not upload in TIIMES. Please use these sections to keep data ready for copy paste.
Data in Item Description columns of Accepted Quantity and cumulative Accepted quantity must be verified thoroughly before uploading in TIIMES.
Pending activity, Areas of concern & Details of measuring instruments sheets are applicable for IVR.
Select options from drop down list for unit of measurement (Item Description) & certifying body of measuring instruments (Details of measuring instruments).
Do not modify this format.
To start next row in cell itself use below shortcut: press 'alt + Enter' keys together. Alt + Enter

## General
Note: - Data filled in this sheet will not upload in TIIMES
Title | Details
Control Number
SAP number
Notification Number
Project Name & Location
Client Name
End User Name
DEC / PMC / EPC Name
DEC / PMC / EPC Number
Vendor Name
PO Number (Client PO on Vendor)
Sub Vendor
PO Number (Vendor PO on Sub Vendor)
Inspection Location
Inspection Date(s)

## Item Description
Po Item No. | Item Code | Item Description | Unit | Po Quantity | Offered Quantity | Accepted Quantity (Please verify thouroghly before using this Column for IRN) | Cumulative Accepted Quanitity (for IRN Only)
1 |  | NIPPLE ,M, B36.10,ASTM A 106 GR B, SEAMLESS , SCH-160 --100 MM LONG SIZE : 1/2 " TH X 1/2" PL | number | 11 | 11 | 11 |  | number
2 |  | NIPPLE ,M, B36.10,ASTM A 106 GR B, PBE, SEAMLESS , SCH-160 --100 MM LONG , SIZE : 3/4 " PL X 3/4" PL | number | 4 | 4 | 4 |  | meter
3 |  | NIPPLE ,M, B36.10,ASTM A 106 GR B, SEAMLESS , SCH-160 --100 MM LONG SIZE : 3/4 " TH X 3/4" PL | number | 1 | 1 | 1 |  | km
4 |  | SWAGE NIPPLE (REDUCER),BW,M,M,BS-3799,ASTM A 105, SIZE : 3/4"BW X 1/2 "BW | number | 1 | 1 | 1 |  | meter (number)
5 |  | PIPE CAP , B16.11, ASTM A 105, SORF , 3000, SIZE : 3/4" TH | number | 1 | 1 | 1 |  | km (number)
6 |  | EQUAL TEE, B16.11,ASTM A105 , SW , 6000 , SIZE : 3/4" | number | 1 | 1 | 1 |  | each
7 |  | GATE VALVE, 3/4" SW, API 602 /ISO 15761,BODY -ASTM A 105,TRIM -STELLITED,STEM-13%CR, STEEL , 800, 6000,B16.11,-OS AND Y BOLTED BONNET , SIZE 3/4 " | number | 1 | 1 | 1 |  | Piece
8 |  | 90 ELBOW, B16.11, ASTM A 105,SW, 6000, SIZE 3/4 " | number | 1 | 1 | 1 |  | Test sample
9 |  | PIPE PL, S-160, B36.10, ASTM A 106 GR B , PE, SEAM LESS , SIZE 1/2 " | meter | 22 | 22 | 22 |  | AU - All Unit
10 |  | SWAGE NIPPLE , M,B36.10, ,ASTM A 106 GR B, PBE, SEAMLESS SIZE : 3/4"PL X 1/2 "PL | number | 6 | 6 | 6 |  | lot
11 |  | NIPPLE , M,B36.10, ,ASTM A 106 GR B, PBE, SEAMLESS 100MM LONG-SCH 160, SIZE : 1/2"PL X 1/2 "PL | number | 4 | 4 | 4 |  | Set
12 |  | EQUAL TEE, B16.11,ASTM A105 , SW , 6000 , SIZE : 1/2" | number | 4 | 4 | 4 |  | Running Meter
13 |  | COUPLING, B16.11,ASTM A105 , 6000 , SIZE : 1/2" TH | number | 5 | 5 | 5 |  | kg
14 |  | 90 ELBOW, B16.11, ASTM A 105,SW, 6000, SIZE 1/2 " | number | 4 | 4 | 4 |  | metric ton (tonne)
15 |  | GATE VALVE, 1/2" SW, API 602 /ISO 15761,BODY -ASTM A 105,TRIM -STELLITED,STEM-13%CR, STEEL , 800, 6000,B16.11,-OS AND Y BOLTED BONNET , SIZE 3/4 " | number | 3 | 3 | 3 |  | ton
16 |  | PIPE CAP , B16.11, ASTM A 105, SORF , 3000, SIZE : 1/2" TH | number | 4 | 4 | 4 |  | cubic millimetre
17 |  | PLUG , SS316 , SIZE 1/2 " OD | number | 6 | 6 | 6 |  | cubic centimeter
18 |  | MALE CONNECTOR , SS316 , SIZE 1/2" NPTM X 1/2" OD | number | 14 | 14 | 14 |  | cubic meter
19 |  | MALE CONNECTOR , SS316 , SIZE 1/4" NPTM X 1/2" OD | number | 6 | 6 | 6 |  | cubic inch
20 |  | TUBE UNION , SS 316 SIZE : 1/2 " OD | number | 13 | 13 | 13 |  | cubic foot
21 |  | SEAMLESS TUBE TO ASTM A 269 TYPE SS316L,1/4"OD X 1 MM THICK EACH LENGTH 5 TO 6 MTR | meter | 72 | 72 | 72 |  | mm
22 |  | PLUG , SS316 , SIZE 1/4 " OD | number | 15 | 15 | 15 |  | cm
23 |  | MALE CONNECTOR , SS316 , SIZE 1/2" NPTM X 1/4" OD | number | 15 | 15 | 15 |  | in
24 |  | MALE CONNECTOR , SS316 , SIZE 1/4" NPTM X 1/4" OD | number | 15 | 15 | 15 |  | foot
25 |  | TUBE UNION , SS 316 SIZE : 1/4 " OD | number | 15 | 15 | 15 |  | mile
26 |  | FLANGE 3/4 NPS, ASME B16.5 , 300 CL , NPT (F) THREADED RF, A182 GR F304 | number | 17 | 17 | 17 |  | yard
27 |  | FEMALE CONNECTOR , SS316 , SIZE 1/2" NPTF X 1/2" OD | number | 3 | 3 | 3 |  | liter
28 |  | TUBE CAP, SS316, SIZE : 1/2 " | number | 3 | 3 | 3 |  | kl
29 |  | SEAMLESS TUBE TO ASTM A 269 TYPE SS316L,1/2"OD X 0.065" THICK EACH LENGTH 5 TO 6 MTR | meter | 65 | 65 | 65 |  | cl
30 |  | EQUAL TEE , SS316 , SIZE : 1/2" OD | number | 3 | 3 | 3 |  | ml
31 |  | GATE VALVE , SS316 -OS , AND Y BOLTED BONNET , SIZE ; 1/2" NPTF -800 | number | 3 | 3 | 3 |  | g
lb
oz
Sq. mm
Sq. cm
Sq. meter
Sq. in
Sq. foot

## Reference Documents
Sr. No. | Document Name | Client Document Number | Vendor Document Number | Approval Status
1 | PR/MR/ARM
2 | QAP/ITP/QCP | A545-4700-5138-QAP-LZ1001-0122 Rev.01 | EX/QP/2021/046 Rev.01 | Approved By JNK
3 | Drawing(s)
4 | Procedure(s)
5 | Datasheet(s)
6 | Others (Specify)

## Stages Witnessed
Stages Witnessed
QAP Sr. No -3.1 ­ Visual check for surface finish /condition on randomly selected 10 % Qty per PO line item – No injurious surface defects were observed­ ­­ Visual found satisfactory.
QAP Sr. No -3.1 ­­Dimension check on randomly selected 10 % Qty per PO line item – All dimensions are within acceptable limit as per Approved drawing ­ -All Dimensions found Acceptable.
QAP Sr. No -3.2 ( a) --Hydrostatic Test For Gate Valve. --Shell Hydrostatic Test witnessed on 10% Qty for Po line 7,15 & 31 -- ­ No Visual Leakage or Pressure Drop Observed at the time of Inspection. Test pressure as per Approved Drg. ­ Acceptable --Backseat Hydrostatic Test witnessed on randomly selected 10 % Qty for Po line 7,15 & 31 - ­ No Visual Leakage or Pressure Drop Observed at the time of inspection. Test pressure as per Approved Drg. --Seat Hydrostatic Test witnessed on randomly selected 10 % Qty for Po line 7,15 & 31 ­ -No Visual Leakage or Pressure Drop Observed at the time of inspection Test pressure as per Approved Drg.
QAP Sr. No -3.2 ( b) --Pneumatic Test For Gate Valve. ­­­Seat Pneumatic Test witnessed on randomly selected 10 % Qty for Po line 7,15 & 31--- No Visual Leakage Observed at the time of Inspection. Test pressure as per standard .

## Document reviewed
Document reviewed
QAP Clause No 1.1: Reviewed Material test certificate for Body ,Bonnet , Stem & Wedge For Gate Valve , found in order
2) QAP Clause No 1.2: Reviewed Material test certificate for Tube Fitting (Body ,Nut ,Ferrule ) and found in order.
QAP Clause No 1.3 : Reviewed Material test certificate for Pipe Fittings & Flanges and found in order
QAP Clause No 1.4 : Reviewed Material test certificate for Tubes & Pipes and ,found to meet material specification requirement.
QAP Note No ­2.1 : Assembly inspection report as declared by vendor reviewed and found in order.
QAP Note No ­11 : Machined surface DP test report of Body , Bonnet , Spindle & wedge of all Gate Valves reviewed and found in order.
Type test report of Tube / fittings as per ASTM F1387 and for Valves MSSP-99 reviewed and found in order.
Calibartion certificates of measuring instruments and Pressure gauges reviewed and found in order

## Details of measuring instrument
Sr. No. | Detail of Equipment(s) / Instrument(s) | Range | ID | Validity till Date | Calibration Certificate Number | NABL / OTHER CERT. BODIES / NABL Traceability (type Yes wherever applicable) | NON-NABL (type Yes wherever applicable)
Yes
No

## Areas of concerns
Areas Of Concern
1.PO SL No-16 (Pipe Cap): As per PO, Required rating is 3000 #, However rating in approved drawing and offered item is 6000 # 2.PO SL No-4 & 10 (Swage Nipple) : Depth of bore is not mentioned in drawing.(observed depth of bore is 24.4mm) 3.PO SL No-21 & 29 (Tubes) : As per PO , Required MOC – Gr 316L ,However offered item MOC – Gr 316 , As per MTC & Marking on Tubes 4. PO SL No-31 (Valve) : As per PO and Approved Drawing , Required MOC -Gr 316 , However offered item MOC – Gr 316 L ,As per marking on valve. 5.PO SL No-1 2,3,10 : There is a typographical error in PO , I) For PO SL 1,2,3 (Nipple):MOC shall be A STM A 106 Gr B instead of ASTM A 105 ,Gr B II) For PO SL 10 (Swage Nipple) :MOC shall be ASTM A 105 only instead of ASTM A 105 Gr B 6.PO SL No-09 (pipe) : Due to unavailability of MTC, marking correlation not done. 7.Heat no /Lot no Not available on fittins and valves 7.As per QAP Clause No : 1& 4 ,CRS ,QAP note :- Document review is balance 8.Dimension report of and Hydro static & pneumatic test report to be submitted

## Pending Activities
Pending Activities from this visit

## Conclusion
Note: Data filled in this sheet will not upload in TIIMES
Non Conformities raised / Discrepancies observed during Inspection (If Any, Mention TUV India NCR Number ):
Identification of Inspected Item(s):
Conclusion (Acceptable / Not Acceptable / Acceptance subject to):
Provisionally acceptable subjected to satisfactory completion of pending activities. Also Refer Area of Concern
IRN can be issued for PO Item numbers:
Expenses:
Remarks: