## Notes
Notes:
Data filled in General and conclusion Sections will not upload in TIIMES. Please use these sections to keep data ready for copy paste.
Data in Item Description columns of Accepted Quantity and cumulative Accepted quantity must be verified thoroughly before uploading in TIIMES.
Pending activity, Areas of concern & Details of measuring instruments sheets are applicable for IVR.
Select options from drop down list for unit of measurement (Item Description) & certifying body of measuring instruments (Details of measuring instruments).
Do not modify this format.
To start next row in cell itself use below shortcut: press 'alt + Enter' keys together. Alt + Enter

## General
Note: - Data filled in this sheet will not upload in TIIMES
Title | Details
Control Number
SAP number
Notification Number
Project Name & Location
Client Name
End User Name
DEC / PMC / EPC Name
DEC / PMC / EPC Number
Vendor Name
PO Number (Client PO on Vendor)
Sub Vendor
PO Number (Vendor PO on Sub Vendor)
Inspection Location
Inspection Date(s)

## Item Description
Po Item No. | Item Code | Item Description | Unit | Po Quantity | Offered Quantity | Accepted Quantity (Please verify thouroghly before using this Column for IRN) | Cumulative Accepted Quanitity (for IRN Only)
1 |  | SS 316L FOAM DISCHARGE HOSE FOR NOZZLE WITH ADAPTOR HOSE LENGTH -850 mm FITTECH APPROVED FABRICATION DRAWING : GIC-AB-2200928-A1351049-001 REV-00 | number | 20 | 20 | 20 | 20 | number
2 |  | SS 316L FOAM DISCHARGE HOSE FOR NOZZLE WITH ADAPTOR HOSE LENGTH -1050 mm FITTECH APPROVED FABRICATION DRAWING : GIC-AB-2200928-A1351049-001 REV-00 | number | 40 | 40 | 40 | 40 | meter
3 |  | SS 316L FOAM DISCHARGE HOSE FOR NOZZLE WITH ADAPTOR HOSE LENGTH -750 mm FITTECH APPROVED FABRICATION DRAWING : GIC-AB-2200928-A1351049-001 REV-00 | number | 40 | 40 | 40 | 40 | km
4 |  | SS 316L FOAM DISCHARGE HOSE FOR NOZZLE WITH ADAPTOR HOSE LENGTH -700 mm FITTECH APPROVED FABRICATION DRAWING : GIC-AB-2200928-A1351049-002 REV-00 | number | 10 | 10 | 10 | 10 | meter (number)
5 |  | CORRUGATES SS HIGH PRESSURE HOSE LENGTH : 6 MTRS FITTECH APPROVED FABRICATION DRAWING : GIC-AB-2200928-A1351049-003 REV-00 | number | 2 | 2 | 2 | 2 | km (number)
6 |  | CORRUGATES SS HIGH PRESSURE HOSE LENGTH : 2.5 MTRS FITTECH APPROVED FABRICATION DRAWING : GIC-AB-2200928-A1351049-003 REV-00 | number | 8 | 8 | 8 | 8 | each
Piece
Test sample
AU - All Unit
lot
Set
Running Meter
kg
metric ton (tonne)
ton
cubic millimetre
cubic centimeter
cubic meter
cubic inch
cubic foot
mm
cm
in
foot
mile
yard
liter
kl
cl
ml
g
lb
oz
Sq. mm
Sq. cm
Sq. meter
Sq. in
Sq. foot

## Reference Documents
Sr. No. | Document Name | Client Document Number | Vendor Document Number | Approval Status
1 | PR/MR/ARM | PT-B18007-B1BUT-LP0008-MEC-P-00-A |  | RIL Document
2 | QAP/ITP/QCP | B26007-PT-B18007-B1BUT-LP0008-MEC-P-00-A-UT342-A05-0001 REV-01 | FE-A05-01 REV-01 | Approved in code-1 by RIL ( Work may proceed )
3 | Drawing(s) | B26007-PT-B18007-B1BUT-LP0008-MEC-P-00-A-UT342-D01-0006 REV-01, B26007-PT-B18007-B1BUT-LP0008-MEC-P-00-A-UT342-D01-0005 REV-01, B26007-PT-B18007-B1BUT-LP0008-MEC-P-00-A-UT342-B02-0008 REV-01 | FE-D01-006 REV-01, FE-D01-005 REV-01, FE-B02-008 REV-01 | Approved in code-1 by RIL ( Work may proceed )
4 | Procedure(s)
5 | Datasheet(s)
6 | Others (Specify)

## Stages Witnessed
Stages Witnessed
As per ITP Clause : 5.7, ( For Foam Discharge Hose) a) Witnessed Final Visual Inspection on 10 % Randomly selected Qty. from each PO Line items - Found free from injurious surface & weld defects.No Visible contaminations observed -Acceptable,Tag details verified on random items from each PO line items - Found ok. B) Witnessed Final dimensional inspection on 10 % Randomly selected Qty. from each PO Line items- Found complying to drawing requirements.Threading checked with gauges & found acceptable c) Witnessed Final hydro test on 10 % Randomly selected Qty. from each PO Line items for a holding period of one minute minimum ( Test pressures as per approved drawings )- No visible leakage nor pressure drop nor deformation observed till the end of testing .Acceptable d) Witnessed Spot PMI Check on all accessible components & welds on 10 % Randomly selected Qty. from each PO Line items-Alloying elements found complying to material specification requirements ( Verified Elements Cr.,Mo., Ni & Mn . ), Verified PMI Machine calibration with a Known Block & found satisfactory.

## Document reviewed
Document reviewed
As per ITP Clause : 2.1 & 2.1, a) Verified WPS / PQR / WPQ documents along with welding consumable certificates - Found complying to drawing requirements .
As per ITP Clause : 5.7, ( For Foam Discharge Hose) a) Reviewed Raw material test certificates / NABL Lab test records as declared by vendor - Found complying to material specification / drawing /ITP requirements
Reviewed Final Test certificate as per EN 10204 3.1 ( MTC No : GIC/8474 Dtd : 30.03.2023 )- Found complying to requirements.

## Details of measuring instrument
Sr. No. | Detail of Equipment(s) / Instrument(s) | Range | ID | Validity till Date | Calibration Certificate Number | NABL / OTHER CERT. BODIES / NABL Traceability (type Yes wherever applicable) | NON-NABL (type Yes wherever applicable)
1 | Vernier Caliper | 0 to 300 mm | 366/04 | 23.12.2023 | 2022-12-366-2294 Dtd : 24.12.2022 | Yes |  | Yes
2 | PMI Machine, Niton XL2 800 |  | 96297 | 20.11.2023 | 21.11.2022 Dtd : 21.11.2022 |  | Yes | No
3 | Taper Thread Plug gauge | 1/2" X 14 NPT | PKY 8458 | 15.05.2023 | 2022/51929/001 Dtd : 16.05.2022 | Yes
4 | Thread Plug Gauge | 1.5 " BSP | SE/8575/1 | 17.12.2023 | ASAE/30/220211 Dtd : 18.12.2022 | Yes
5 | Pressure gauge | 0 to 42 Kg/cm2g | 19122191010 8 | 18.11.2023 | 2022-11-307-1841 Dtd : 19.11.2022 | Yes
6 | Thread Ring gauge ( NoGo) | 1/2 " X 14 BSP | SM-144 | 28.01.2024 | ASAE/32/220326 Dtd : 19.01.2023 | Yes
7 | Thread Ring gauge ( Go) | 1/2 " BSP | --- | 28.01.2024 | ASAE/32/220325 Dtd : 19.01.2023 | Yes
8 | Thread Plug Gauge | 1 " X 11 BSP | 51180/003 | 25.03.2024 | 2023/51180/003 Dtd : 26.03.2023 | Yes
9 | Thread Plug Gauge | 1/2" X 14BSP | 50494/003 | 20.02.2024 | 2023/50494/003 Dtd : 21.02.2023 | Yes
10 | Measuring Tape | 0 to 5 Mtrs | 190514N | 24.12.2023 | 2022-12-366-2291 Dtd : 24.12.2022 | Yes
11 | Measuring Tape | 0 to 30 Mtrs | F118-15 | 24.12.2023 | 2022-12-366-2291 Dtd : 24.12.2022 | Yes

## Areas of concerns
Areas Of Concern

## Pending Activities
Pending Activities from this visit
None

## Conclusion
Note: Data filled in this sheet will not upload in TIIMES
Non Conformities raised / Discrepancies observed during Inspection (If Any, Mention TUV India NCR Number ):
Identification of Inspected Item(s):
Conclusion (Acceptable / Not Acceptable / Acceptance subject to):
IRN can be issued for PO Item numbers:
Expenses:
Remarks: