## Notes
Notes:
Data filled in General and conclusion Sections will not upload in TIIMES. Please use these sections to keep data ready for copy paste.
Data in Item Description columns of Accepted Quantity and cumulative Accepted quantity must be verified thoroughly before uploading in TIIMES.
Pending activity, Areas of concern & Details of measuring instruments sheets are applicable for IVR.
Select options from drop down list for unit of measurement (Item Description) & certifying body of measuring instruments (Details of measuring instruments).
Do not modify this format.
To start next row in cell itself use below shortcut: press 'alt + Enter' keys together. Alt + Enter

## General
Note: - Data filled in this sheet will not upload in TIIMES
Title | Details
Control Number
SAP number
Notification Number
Project Name & Location
Client Name
End User Name
DEC / PMC / EPC Name
DEC / PMC / EPC Number
Vendor Name
PO Number (Client PO on Vendor)
Sub Vendor
PO Number (Vendor PO on Sub Vendor)
Inspection Location
Inspection Date(s)

## Item Description
Po Item No. | Item Code | Item Description | Unit | Po Quantity | Offered Quantity | Accepted Quantity (Please verify thouroghly before using this Column for IRN) | Cumulative Accepted Quanitity (for IRN Only)
1 | J2662ASFPN005 | J2662A ,PART NO. 5,SHELL FRONT FLANGE - SIZE : 1213 MM OD X 1020 MM ID X 82+40.5 MM THK ; SA-266 CL.2 OF ASME SEC. II PART A | number | 1 | 1 | 1 | 1 | number
2 | J2662FHFPNO103 | J2662A, FLOATING HEAD FLANGE - SIZE: 1012 MM OD X 899 MM ID X 103 MM THK ; SA-266 CL.2 OF ASME SEC. II PART A | number | 1 | 1 | 1 | 1 | meter
3 | J2662ACFPNO52 | J2662A ,PART NO. 52,CHANNEL FLANGE - SIZE : 1213 MM OD X 1020 MM ID X 93+31.5 MM THK ; SA-266 CL.2 OF ASME SEC. II PART A | number | 1 | 1 | 1 | 1 | km
4 | J2662ACCFPNO53 | J2662A ,PART NO. 53,CHANNEL COVER FLANGE - SIZE : 1202 MM OD X 1020 MM ID X 93+31.5 MM THK ; SA-266 CL.2 OF ASME SEC. II PART A | number | 1 | 1 | 1 | 1 | meter (number)
5 | J2662ACCPNO54 | J2662A,CHANNEL COVER - SIZE : 1202 MM OD X 86 +13MM THK ; SA-266 CL.2 OF ASME SEC. II PART A | number | 1 | 1 | 1 | 1 | km (number)
6 | J2662ASTPNO101 | J2662A ,PART NO. 101,STATIONARY TUBE SHEET - SIZE : 1107 MM OD X 88 MM THK ; SA-266 CL.2 OF ASME SEC. II PART A | number | 1 | 1 | 1 | 1 | each
7 | J2662AFTPNO102 | J2662A ,PART NO. 102,FLOATING TUBE SHEET - SIZE : 1012 MM OD X 88 MM THK ; SA-266 CL.2 OF ASME SEC. II PART A | number | 1 | 1 | 1 | 1 | Piece
8 | J2664ASTPNO101 | J2664A ,PART NO. 101,STATIONARY TUBE SHEET - SIZE : 1183 MM OD X 88 MM THK ; SA-266 CL.2 OF ASME SEC. II PART A | number | 1 | 1 | 1 | 1 | Test sample
9 | J2664AFTPNO102 | J2664A ,PART NO. 102,FLOATING TUBE SHEET - SIZE : 1092 MM OD X 88 MM THK ; SA-266 CL.2 OF ASME SEC. II PART A | number | 1 | 1 | 1 | 1 | AU - All Unit
lot
Set
Running Meter
kg
metric ton (tonne)
ton
cubic millimetre
cubic centimeter
cubic meter
cubic inch
cubic foot
mm
cm
in
foot
mile
yard
liter
kl
cl
ml
g
lb
oz
Sq. mm
Sq. cm
Sq. meter
Sq. in
Sq. foot

## Reference Documents
Sr. No. | Document Name | Client Document Number | Vendor Document Number | Approval Status
1 | PR/MR/ARM | TDC/J2662/022 REV.00 Dt. 02.09.2023, For Item No. 1 & 2. TDC/J2662/012 REV.00 Dt. 02.09.2023, For Item No. 3, 4 & 5. TDC/J2662/011 REV.00 Dt. 02.09.2023, For Item No. 6 & 7. TDC/J2664/001 REV.00 Dt. 02.09.2023, For Item No. 8 & 9. |  | Approved by ACOUSTICS
2 | QAP/ITP/QCP | RDF/ACOUS/10390 REV.1 Dt. 12.10.2023 |  | Approved by ACOUSTICS
3 | Drawing(s) | As mentioned in PO |  | Approved by ACOUSTICS
4 | Procedure(s)
5 | Datasheet(s)
6 | Others (Specify) | SA-266 CL.2 of ASME Sec. II Part A Ed: 2021 and scope of inspection as mentioned in client's mail dated: 13.11.2023 |  | Applicable

## Stages Witnessed
Stages Witnessed
Witnessed Ultrasonic Test @100% as per ASTM A-388 and acceptance criteria as per 3.3.4 of ASME Sec. VIII Div. 2 Ed: 2021 for item no. 2, 6, 7, 8 & 9, found acceptable.
Witness Hardness @100% and observations found within acceptable limits as per client's specification, found acceptable.
Witnessed Visual, Marking and Dimesion as per PO & approved drawing @100%, found acceptable.

## Document reviewed
Document reviewed
Raw Material Test certificate and Heat Treatment chart reviewed as per client's and material specification, found acceptable.
Reviewed Product Analysis and Mechanical Test values as per client's and material specification, found acceptable.
Reviewed internal UT report for item no. 1,3,4 & 5 as per client's requirement, found acceptable.
Reviewed internal LPT report as per client's requirement, found acceptable.
Manufacturer test certificates number 17719 Date: 16.11.23 reviewed and endorsed.

## Details of measuring instrument
Sr. No. | Detail of Equipment(s) / Instrument(s) | Range | ID | Validity till Date | Calibration Certificate Number | NABL / OTHER CERT. BODIES / NABL Traceability (type Yes wherever applicable) | NON-NABL (type Yes wherever applicable)
1 | Vernier Calliper | 0-300 MM | RDF12430 | 20.11.23 | BCL/2022/13118F, 23.11.22 | Yes |  | Yes
2 | Vernier Calliper | 0-1000 MM | 815130038 | 02.07.24 | BCL/2023/05936F, 03.07.23 | Yes |  | No
3 | Vernier Calliper | 0-2000 MM | RDF-VC-50 | 28.08.24 | BCL/2023/08091F, 29.08.23 | Yes

## Areas of concerns
Areas Of Concern

## Pending Activities
Pending Activities from this visit

## Conclusion
Note: Data filled in this sheet will not upload in TIIMES
Non Conformities raised / Discrepancies observed during Inspection (If Any, Mention TUV India NCR Number ):
Identification of Inspected Item(s):
Conclusion (Acceptable / Not Acceptable / Acceptance subject to):
IRN can be issued for PO Item numbers:
Expenses:
Remarks:
Inspected items identified with TUV low stress Hard stamped as “ ” near manufacturers marking. (Double on witnessed & rest single)