## Notes
Notes:
Data filled in General and conclusion Sections will not upload in TIIMES. Please use these sections to keep data ready for copy paste.
Data in Item Description columns of Accepted Quantity and cumulative Accepted quantity must be verified thoroughly before uploading in TIIMES.
Pending activity, Areas of concern & Details of measuring instruments sheets are applicable for IVR.
Select options from drop down list for unit of measurement (Item Description) & certifying body of measuring instruments (Details of measuring instruments).
Do not modify this format.
To start next row in cell itself use below shortcut: press 'alt + Enter' keys together. Alt + Enter

## General
Note: - Data filled in this sheet will not upload in TIIMES
Title | Details
Control Number
SAP number | 8120174575
Notification Number | 2022-179344
Project Name & Location
Client Name
End User Name
DEC / PMC / EPC Name
DEC / PMC / EPC Number
Vendor Name
PO Number (Client PO on Vendor)
Sub Vendor
PO Number (Vendor PO on Sub Vendor)
Inspection Location | m & k, kolhapur
Inspection Date(s) | 17.10.2022 & IRN-7.11.2022

## Item Description
Po Item No. | Item Code | Item Description | Unit | Po Quantity | Offered Quantity | Accepted Quantity (Please verify thouroghly before using this Column for IRN) | Cumulative Accepted Quanitity (for IRN Only)
------ | ------ | RIL to PCT PO No.-314/240387094 Dated 18.08.2021 Project -PL2101 PROCESS COMBUSTION TECHNOLOGIES INDIA PRIVATE LIMITED PO on- THERMAX BABCOCK & WILCOX ENERGY SOLUTIONS LTD -PCT/4627/00027 / 19.10.2021 | [5 empty] | number
00010 | ------ | WASTE HEAT RECOVERY BOILER PACKAGE | Set | 1 |  |  |  | meter
------ | ------ | THERMAX BABCOCK & WILCOX ENERGY SOLUTIONS LTD. PO on M/S M & K INDUSTRIES - 776005441DT-18.05.2022 | [5 empty] | km
4 | A3508300000 | ASS & DETAILS OF HAND RAILING S16-3WH-508300-R 01 (for details refer attached Annexure I ) | Piece | 1 | 1 | 1 |  | meter (number)
5 | A3508301000 | ASS & DETAILS OF HAND RAILING S16-3WH-508301-R 01 (for details refer attached Annexure I ) | Piece | 1 | 1 | 1 |  | km (number)
each
Piece
Test sample
AU - All Unit
lot
Set
Running Meter
kg
metric ton (tonne)
ton
cubic millimetre
cubic centimeter
cubic meter
cubic inch
cubic foot
mm
cm
in
foot
mile
yard
liter
kl
cl
ml
g
lb
oz
Sq. mm
Sq. cm
Sq. meter
Sq. in
Sq. foot

## Reference Documents
Sr. No. | Document Name | Client Document Number | Vendor Document Number | Approval Status
1 | PR/MR/ARM | -------- | -------- | --------
2 | QAP/ITP/QCP | INSPECTION AND TEST PLAN BOILER NON PRESSURE PART MT-B21P01-D1BPN-MB-C001-ME-CP-00A-PN212-A05-0011-Rev.02 | PCTL document no.-4627-QA-SP-ITP-010-I Rev. 02 THERMAX BABCOCK & WILCOX ENERGY SOLUTIONS PRIVATE LIMITED (TBWE)- Document - INSPECTION & TEST PLAN (QA PLAN) FOR-BOILER STRUCTURE-- CONTROL NO.: ITP/ PL2101 /N51 REVISION NO. : 02 | RIL approved.Code -1, PCC- approved
3 | Drawing(s) | -------- | S16-3WH-508300-R 01 S16-3WH-508301-R 01 | TBWE Document
4 | Procedure(s) | Paint Specification MT­B21P01­ D1BPNMB­C001­ME­CP­00A PN212­J04­0001 Rev. 03 Paint Procedure MT­B21P01­ D1BPNMB­C001­ME­CP­00A PN212­J04­0003Rev. 01 | PAINTING SPECIFICATION FOR BOILER PACKAGE 4627­PM­PRO­PAINTING­001­I Rev.03 PAINTING PROCEDURE FOR BOILER PACKAGE 4627­PM­PRO­PAINTING­003­I Rev. 01 | RIL approved.Code ­1,
5 | Datasheet(s) | -------- | -------- | --------
6 | Others (Specify) | RP­MS­ENGG­SPC­PP014 REV. R0 RP­MS­ENGG­SPC-CS002 REV. R0 RP­MS­ENGG­SPC-CS014 REV. R0 | -------- | RIL Specifications

## Stages Witnessed
Stages Witnessed
ITP SR.NO. -19-PAINTING INSPECTION (scope- RW -10%) Paint inspection done at random locations / parts as offered by vendor and as below: Paint shade verified and found in order as Golden yellow. Visual inspection carried out for Complete coverage of area. The paint defects rundowns, Peeloffs, Cracks etc. not observed. Hence accepted. Paint DFT checked at random location and found within limit & acceptale. Adhesion test witnessed at random locations/parts and results observed satisfactory. The Pull of adhesion Test carried out on test coupon. The results observed above 5 MPa. Test accepted. Verification of Identification Marking-The parts were marked with permanent marker for details viz. part no., drawing no. etc. by vendor..

## Document reviewed
Document reviewed
ITP SR.NO. 1 Material identification Heat chart & Material TCs, reviewed and found in order.
ITP SR.NO.2 Review of WPS / PQR /WPQ Weld documents reviewed and found in order.
ITP SR.NO. 18 Surface preparation & 19 paintinginspection: TBWE report, salt contamination /surface preparation reports, Dolly test results reviewed and found in order. Adhesion test report reviewed and found in order. Paint report, Paint TC reviewed and found in order. Annexure reviewed and found in order.

## Details of measuring instrument
Sr. No. | Detail of Equipment(s) / Instrument(s) | Range | ID | Validity till Date | Calibration Certificate Number | NABL / OTHER CERT. BODIES / NABL Traceability (type Yes wherever applicable) | NON-NABL (type Yes wherever applicable)
1 | Digital coating thickness meter | 0­20/1250 micron m | MK/CM/01 | 19.02.2023 | PI220220­9­21 | Yes |  | Yes
2 | Adhesion Tester ( dolly test) | 0­20 MPa | AT07812 | 14.09.2023 | 2268 |  | Yes | No

## Areas of concerns
Areas Of Concern

## Pending Activities
Pending Activities from this visit

## Conclusion
Note: Data filled in this sheet will not upload in TIIMES
Non Conformities raised / Discrepancies observed during Inspection (If Any, Mention TUV India NCR Number ):
Identification of Inspected Item(s):
part number, drawing number etc. marking done by vendor on parts with permanent marker.
Conclusion (Acceptable / Not Acceptable / Acceptance subject to):
The offered inspection stage activities acceptable .
IRN can be issued for PO Item numbers:
Expenses:
Remarks: