## Notes
Notes:
Data filled in General and conclusion Sections will not upload in TIIMES. Please use these sections to keep data ready for copy paste.
Data in Item Description columns of Accepted Quantity and cumulative Accepted quantity must be verified thoroughly before uploading in TIIMES.
Pending activity, Areas of concern & Details of measuring instruments sheets are applicable for IVR.
Select options from drop down list for unit of measurement (Item Description) & certifying body of measuring instruments (Details of measuring instruments).
Do not modify this format.
To start next row in cell itself use below shortcut: press 'alt + Enter' keys together. Alt + Enter

## General
Note: - Data filled in this sheet will not upload in TIIMES
Title | Details
Control Number
SAP number
Notification Number
Project Name & Location
Client Name
End User Name
DEC / PMC / EPC Name
DEC / PMC / EPC Number
Vendor Name
PO Number (Client PO on Vendor)
Sub Vendor
PO Number (Vendor PO on Sub Vendor)
Inspection Location
Inspection Date(s)

## Item Description
Po Item No. | Item Code | Item Description | Unit | Po Quantity | Offered Quantity | Accepted Quantity (Please verify thouroghly before using this Column for IRN) | Cumulative Accepted Quanitity (for IRN Only)
1 | 5002065020452 | Root Air Blower Capcity 750 M3/hr x 0.65 kg/cm2(g) with all accessories Model number :: UGRK -240,Mfr.sr no : 22230336 & 22230337 MOC of Blower body : IS 210 FG 300,Motor : 40 HP 1450 RPM MOC of Shaft : EN 19 BS970 MOC of Gear : EN 353 BS970 | number | 2 | 2 | 2 | 2 | number
2 | 5002065020451 | Root Air Blower Capcity 925 M3/hr x 0.55 kg/cm2(g) with all accessories Model number :: UGRK -240,Mfr.sr no : 22230338 & 22230339 MOC of Blower body : IS 210 FG 300,Motor : 40 HP 1450 RPM MOC of Shaft : EN 19 BS970 MOC of Gear : EN 353 BS970 | number | 2 | 2 | 2 | 2 | meter
km
meter (number)
km (number)
each
Piece
Test sample
AU - All Unit
lot
Set
Running Meter
kg
metric ton (tonne)
ton
cubic millimetre
cubic centimeter
cubic meter
cubic inch
cubic foot
mm
cm
in
foot
mile
yard
liter
kl
cl
ml
g
lb
oz
Sq. mm
Sq. cm
Sq. meter
Sq. in
Sq. foot

## Reference Documents
Sr. No. | Document Name | Client Document Number | Vendor Document Number | Approval Status
1 | PR/MR/ARM | Not Applicable | Not Applicable | Not Applicable
2 | QAP/ITP/QCP | -- | RD/101/13-14 Rev.00 | Approved by BEIL
3 | Drawing(s) | -- | GA-2223016 Rev.00 & GA-2223017 Rev.00 | Approved by BEIL
4 | Procedure(s) | Not Applicable | Not Applicable | Not Applicable
5 | Datasheet(s) | Not Applicable | Not Applicable | Not Applicable
6 | Others (Specify) | Not Applicable | Not Applicable | Not Applicable

## Stages Witnessed
Stages Witnessed
ITP Stage no: 3.0 -Verified Identification of Blower. -Witnessed Perfomnace test of root Blower as per approved drawing technical parameter & BS 1571 part II requirements.Verified Speed,currnet,voltage,Vibration in three direction,Main body,outer cover tempratre,suction & discharge pressure ,Exhaust Air temprature & Noise level-found acceptable.

## Document reviewed
Document reviewed
ITP Stage no: 1.0 -Reviewed material test certificate & Lab test report for Blower body,outer cover,Lobe,shaft & gear-found to meet the Specification requirements.
ITP Stage no: 2.1 -Reviewed Dynemic balancing report of Rotor-found in order.
ITP Stage no: 2.2 -Reviewed Hydrotest report for casing & side Cover-found in order.

## Details of measuring instrument
Sr. No. | Detail of Equipment(s) / Instrument(s) | Range | ID | Validity till Date | Calibration Certificate Number | NABL / OTHER CERT. BODIES / NABL Traceability (type Yes wherever applicable) | NON-NABL (type Yes wherever applicable)
1 | Digital thermometer | -- | DT-01 | 12.12.2022 | 20211213-3961-11 dated 13.12.2021 |  | Yes | Yes
2 | Digital Clamp meter | 0-1200 A | 1080-18010892 | 12.12.2022 | 20211213-3961-12 dated 13.12.2021 |  | Yes | No
3 | Infrared Thermeter | 18-275 c | 32970573 | 12.12.2022 | 20211213-3961-13 dated 13.12.2021 |  | Yes
4 | scale of double limbed water filled | 0-1000mm | MS-03 | 12.12.2022 | 20211213-3961-19 dated 13.12.2021 |  | Yes
5 | scale of mercury filled Barometer | 640-810 mm | MS-01 | 12.12.2022 | 20211213-3961-20 dated 13.12.2021 |  | Yes
6 | scale of mercury filled Barometer | 0-1000 MM | MS-02 | 12.12.2022 | 20211213-3961-21 dated 13.12.2021 |  | Yes
7 | sound level meter | 30-130 db | SL-4030 | 12.12.2022 | 20211213-3961-22 dated 13.12.2021 |  | Yes
8 | Tachometer | 0-99999RPM | 18-812 | 12.12.2022 | 20211213-3961-24 dated 13.12.2021 |  | Yes
9 | Vibration meter | -- | 0815-2408 | 12.12.2022 | 20211213-3961-25 dated 13.12.2021 |  | Yes
10 | Steel scale | 0-1000 mm | 401FR | 12.12.2022 | 20211213-3961-23 dated 13.12.2021 |  | Yes

## Areas of concerns
Areas Of Concern
--

## Pending Activities
Pending Activities from this visit
NIL

## Conclusion
Note: Data filled in this sheet will not upload in TIIMES
Non Conformities raised / Discrepancies observed during Inspection (If Any, Mention TUV India NCR Number ):
Identification of Inspected Item(s):
Conclusion (Acceptable / Not Acceptable / Acceptance subject to):
IRN can be issued for PO Item numbers:
Expenses:
Remarks: