## Notes
Notes:
Data filled in General and conclusion Sections will not upload in TIIMES. Please use these sections to keep data ready for copy paste.
Data in Item Description columns of Accepted Quantity and cumulative Accepted quantity must be verified thoroughly before uploading in TIIMES.
Pending activity, Areas of concern & Details of measuring instruments sheets are applicable for IVR.
Select options from drop down list for unit of measurement (Item Description) & certifying body of measuring instruments (Details of measuring instruments).
Do not modify this format.
To start next row in cell itself use below shortcut: press 'alt + Enter' keys together. Alt + Enter

## General
Note: - Data filled in this sheet will not upload in TIIMES
Title | Details
Control Number
SAP number
Notification Number
Project Name & Location
Client Name
End User Name
DEC / PMC / EPC Name
DEC / PMC / EPC Number
Vendor Name
PO Number (Client PO on Vendor)
Sub Vendor
PO Number (Vendor PO on Sub Vendor)
Inspection Location | wilo m n p-kolhapur
Inspection Date(s) | 21.10.2023

## Item Description
Po Item No. | Item Code | Item Description | Unit | Po Quantity | Offered Quantity | Accepted Quantity (Please verify thouroghly before using this Column for IRN) | Cumulative Accepted Quanitity (for IRN Only)
. | . | AARTI INDUSTRIES LTD's Purchse Order on Shah Traders-4550418279 dt- 23.06.2023 Shah Traders Purchse Order on WILO MATHER & PLATT PUMPS PRIVATE LIMITED-143/2023-2024 dt- 27-Jun-23 | [5 empty] | number
10 | CH000127014 | SS316 CENT PUMP Make & Model : WILO/ PISO 40-200 (WILO scope of supply -bare pump, mechanical seal, motor ) Pump sr.no. -81334358/10/1 & 2 | number | 2 | 2 | 2 | 2 | meter
km
meter (number)
km (number)
each
Piece
Test sample
AU - All Unit
lot
Set
Running Meter
kg
metric ton (tonne)
ton
cubic millimetre
cubic centimeter
cubic meter
cubic inch
cubic foot
mm
cm
in
foot
mile
yard
liter
kl
cl
ml
g
lb
oz
Sq. mm
Sq. cm
Sq. meter
Sq. in
Sq. foot

## Reference Documents
Sr. No. | Document Name | Client Document Number | Vendor Document Number | Approval Status
1 | PR/MR/ARM
2 | QAP/ITP/QCP |  | WILO std. QAP- QA-02-20 ,Cat II Rev .01 dt-12.12.2016 | AIL Approved
3 | Drawing(s) |  | General Arrangement drg. - 81334358-10-GA-Rev. 02 , CSD /cross section drawing -81334358/ PISO 40-200/ CSD Rev. 00 | AIL-code -1- Approved, AIL-code -5- Retained for information
4 | Procedure(s)
5 | Datasheet(s) |  | Technical DataSheet & Ref.performance curve -40-200_50_4_A_R02 | AIL-code -5- Retained for information
6 | Others (Specify)

## Stages Witnessed
Stages Witnessed
QAP cl -6-Final Inspetion :- Performance test with Job motor ( scope - 1per type/size) The following pump /sr.no.s for performance witnessed at WILO. The pump with job motor, run for 1 hr. at rated paramteres & then performance testing carried out. During the test various paramters viz. RPM, flow , head, Power , vibration, noise level, bearing temp . etc. recorded. The test results observed satisfactory. For details refer the pump test performance reports. Pump sr.no. -81334358/10/ 1 , Motor sr.no.-WIAM17352

## Document reviewed
Document reviewed
QAP cl 1/2/3- Casing/impeller /shaft - Mfg. COC reviewed and found in order.
QAP cl 4- Casing -hydro test:- Mfg. COC reviewed and found in order.
QAP cl 5- impeller-dynamic balancing- Mfg. COC reviewed and found in order.
QAP cl 6- Performance test reports for all witnessed and non witnessed pumps reviewed and found in order.
Calibration test reports /annexure reviewed and found in order.
Wilo compliance reviewed and found in order.

## Details of measuring instrument
Sr. No. | Detail of Equipment(s) / Instrument(s) | Range | ID | Validity till Date | Calibration Certificate Number | NABL / OTHER CERT. BODIES / NABL Traceability (type Yes wherever applicable) | NON-NABL (type Yes wherever applicable)
1 | refer attached Annexure -1 for instruments used during the testing. |  |  |  |  | Yes | Yes | Yes
No

## Areas of concerns
Areas Of Concern

## Pending Activities
Pending Activities from this visit

## Conclusion
Note: Data filled in this sheet will not upload in TIIMES
Non Conformities raised / Discrepancies observed during Inspection (If Any, Mention TUV India NCR Number ):
Identification of Inspected Item(s):
1)Pump sr.no. hard punched on the suction flange OD by WILO. 2)TUV hard stamp punched as " " for witnessed pump & as " " for non witnessed pump, near pump sr.no. on the Suction flange OD.
Conclusion (Acceptable / Not Acceptable / Acceptance subject to):
IRN can be issued for PO Item numbers:
Expenses:
Remarks: