## Notes
Notes:
Data filled in General and conclusion Sections will not upload in TIIMES. Please use these sections to keep data ready for copy paste.
Data in Item Description columns of Accepted Quantity and cumulative Accepted quantity must be verified thoroughly before uploading in TIIMES.
Pending activity, Areas of concern & Details of measuring instruments sheets are applicable for IVR.
Select options from drop down list for unit of measurement (Item Description) & certifying body of measuring instruments (Details of measuring instruments).
Do not modify this format.
To start next row in cell itself use below shortcut: press 'alt + Enter' keys together. Alt + Enter

## General
Note: - Data filled in this sheet will not upload in TIIMES
Title | Details
Control Number
SAP number
Notification Number
Project Name & Location
Client Name
End User Name
DEC / PMC / EPC Name
DEC / PMC / EPC Number
Vendor Name
PO Number (Client PO on Vendor)
Sub Vendor
PO Number (Vendor PO on Sub Vendor)
Inspection Location
Inspection Date(s)

## Item Description
Po Item No. | Item Code | Item Description | Unit | Po Quantity | Offered Quantity | Accepted Quantity (Please verify thouroghly before using this Column for IRN) | Cumulative Accepted Quanitity (for IRN Only)
5 | 2000022428 | TBE HT TRNSF MET 25.40 MM 12 BWG 12200 MM [25.4 mm OD X 2.77 mm Thk. X 12200 mm Long ASTM A 179 Tubes Finned With SB 209 Alloy 1060 Fin, 57 mm Fin OD X 0.40 mm Fin Thk., 433 FPM, "G" Type Finning] | each | 1512 | 612 | 612 | 1512 | number
meter
km
meter (number)
km (number)
each
Piece
Test sample
AU - All Unit
lot
Set
Running Meter
kg
metric ton (tonne)
ton
cubic millimetre
cubic centimeter
cubic meter
cubic inch
cubic foot
mm
cm
in
foot
mile
yard
liter
kl
cl
ml
g
lb
oz
Sq. mm
Sq. cm
Sq. meter
Sq. in
Sq. foot

## Reference Documents
Sr. No. | Document Name | Client Document Number | Vendor Document Number | Approval Status
1 | PR/MR/ARM | Not applicable. | Not applicable. | Not applicable.
2 | QAP/ITP/QCP | Not applicable. | AK/ITP/JAL/1253 Rev. 00 Dt. 09.11.2022. | Approved by Reliance Industries Ltd. On Dt. 14.11.2022
3 | Drawing(s) | Not applicable. | AK/DRG/JAL/1253 Rev. 00 Dt. 09.11.2022 | Approved by Reliance Industries Ltd. Via e-mail Dt. 19.07.2022
4 | Procedure(s) | Not applicable. | Not applicable. | Not applicable.
5 | Datasheet(s) | Not applicable. | Not applicable. | Not applicable.
6 | Others (Specify) | 1) Client Specification : - PSIR-063 Rev03 & PSIR-040 Rev 01. 2) EIL Specification no :- 6-15-52 (Rev0) 3) E-mail confirmation Dt. 05.01.2023 received from M/s. RIL regarding, hydro test pressure. | Not applicable. | Provided by M/s. RIL.

## Stages Witnessed
Stages Witnessed
ITP Sr. No. 3.0 (Final Inspection Report): 3.2 (Physical Condition): A) Visual inspection carried out on 10% randomly selected finned tubes from offered lot - Found free of injurious surface defects. B) Overall Dimension inspection carried out 10% randomly selected finned tubes from offered lot - Found to meet the drawing requirement. C) Visual inspection carried out (100%) for bare end (unfinned area) & at accessible area - Found free of injurious defects. D) Marking verification carried out on sticker for 10% randomly selecetd finned tubes - Found in order.
ITP Sr. No. 3.0 (Final Inspection Report): 3.3 (Hydro Test) A) Hydro test witnessed on 10% randomly selected finned tubes from offered lot at 62 Kg/cm2 (g) pressure [Required pressure: 60 Kg/cm2 (g)] in horizontal position - No leakage or Pressure drop observed during the holding period of 10 seconds.
- All measuring instruments/ equipment were verified for continued suitability for intended use, proper identification, calibration status, traceability to national standards & found satisfactory.

## Document reviewed
Document reviewed
- Calibration certificates of Measuring and Testing instrument reviewed - Found to meet the requirement.
ITP Sr. No. 1.0 (Raw Material (1.1-3.0 (Final Inspection Report): - Bare tube material test certificate along with material identification report reviewed for its contents and as declared by supplier / manufacturer endorsed by (APTPL) :- Found to meet the QAP, drawing, client specification & relevant material specification requirements.
ITP Serial No 2.1, 2.2 & 2.3, - Aluminium fin strip material test certificate along with material identification report and PMI reports reviewed for its contents and as declared by supplier/manufacturer. (endorsed by APTPL) - Found to meet the QAP, drawing, client specification & relevant material specification requirements.
ITP Serical No 3.1. - Pull-out test report to check mechanical bonding - Found satisfactory.
Inprocess inspection reports, Drying & Preservation inspection report, Packing list and Marking - Found in order.

## Details of measuring instrument
Sr. No. | Detail of Equipment(s) / Instrument(s) | Range | ID | Validity till Date | Calibration Certificate Number | NABL / OTHER CERT. BODIES / NABL Traceability (type Yes wherever applicable) | NON-NABL (type Yes wherever applicable)
1 | Pressure Gague | 0 to 210 Kg/Cm2 | PG/210KG/CM2/01 | 2023-07-19 | MH/CL/22/07/132 Date. 20-07-2022 | No |  | Yes
2 | Pressure Gague | 0 to 210 Kg/Cm2 | PG/210KG/CM2/02 | 2023-07-19 | MH/CL/22/07/133 Date. 20-07-2022 | No |  | No
3 | Measuring Tape | 1-15 Mtr | MT/15Mtrs/01 | 2023-05-10 | MH/CL/074B/NABL Date. 12-05-2023 | Yes
4 | Steel Scale | 0 to 300 mm | SS/300MM/01 | 2023-08-09 | MH/CL/22/08/349/NABL Date. 10-08-2022 | Yes
5 | Vernier Caliper | 0 to 300 mm | 3219686 | 2023-08-17 | MH/CL/22/08/524/NABL Date. 18-08-2022 | Yes
6 | Digital Micrometer | 0-25 mm | 190431684 | 2023-07-14 | MH/CL/22/07/417/NABL Date. 15-07-2022 | Yes

## Areas of concerns
Areas Of Concern
- None.

## Pending Activities
Pending Activities from this visit
- None.

## Conclusion
Note: Data filled in this sheet will not upload in TIIMES
Non Conformities raised / Discrepancies observed during Inspection (If Any, Mention TUV India NCR Number ):
None.
Identification of Inspected Item(s):
10% randomly selecetd and Hydro test witnessed tubes are identified with double & rest of all single soft stamp as "TUV" (Round) on sticker & attached at bare end A for identification.
Conclusion (Acceptable / Not Acceptable / Acceptance subject to):
Acceptable.
IRN can be issued for PO Item numbers:
No, not for all the items.
Expenses:
Remarks: