## Notes
Notes:
Data filled in General and conclusion Sections will not upload in TIIMES. Please use these sections to keep data ready for copy paste.
Data in Item Description columns of Accepted Quantity and cumulative Accepted quantity must be verified thoroughly before uploading in TIIMES.
Pending activity, Areas of concern & Details of measuring instruments sheets are applicable for IVR.
Select options from drop down list for unit of measurement (Item Description) & certifying body of measuring instruments (Details of measuring instruments).
Do not modify this format.
To start next row in cell itself use below shortcut: press 'alt + Enter' keys together. Alt + Enter

## General
Note: - Data filled in this sheet will not upload in TIIMES
Title | Details
Control Number
SAP number | 8116951448
Notification Number | Email Dt 25.04.2022
Project Name & Location | DDP JMD SEZ Site
Client Name | Reliance Industries Limited
End User Name | Reliance Industries Limited
DEC / PMC / EPC Name | NA
DEC / PMC / EPC Number | NA
Vendor Name | M/s. Boldrocchi India Pvt Ltd, Irungatukottai.
PO Number (Client PO on Vendor) | HPRJ/MWL/7753149 Dt.13.01.2021 (BI Job No : VR00724)
Sub Vendor | NA
PO Number (Vendor PO on Sub Vendor) | NA
Inspection Location | M/s. Boldrocchi India Pvt Ltd, Irungatukottai.
Inspection Date(s) | 26.04.2022

## Item Description
Po Item No. | Item Code | Item Description | Unit | Po Quantity | Offered Quantity | Accepted Quantity (Please verify thouroghly before using this Column for IRN) | Cumulative Accepted Quanitity (for IRN Only)
1 | 4500633094 | ATM. ABSORBER OFF GAS BLOWER, Tag No: C1 540,Model No : 45L-126/280 M SWSI (EXCEPT SEAL STATION AND EXPANSION JOINT) | each | 1 | 1 | 1 | 1 | number
2 | 4500640878 | ATM. ABSORBER OFF GAS BLOWER, Tag No: C2 540, Model No : 45L-126/280 M SWSI (EXCEPT SEAL STATION AND EXPANSION JOINT) | Each | 1 | 1 | 1 | 1 | meter
km
meter (number)
km (number)
each
Piece
Test sample
AU - All Unit
lot
Set
Running Meter
kg
metric ton (tonne)
ton
cubic millimetre
cubic centimeter
cubic meter
cubic inch
cubic foot
mm
cm
in
foot
mile
yard
liter
kl
cl
ml
g
lb
oz
Sq. mm
Sq. cm
Sq. meter
Sq. in
Sq. foot

## Reference Documents
Sr. No. | Document Name | Client Document Number | Vendor Document Number | Approval Status
1 | PR/MR/ARM | MT-HA0003-H1HPT- MAF001-MEC-P-00-A | NIL | OF RIL
2 | QAP/ITP/QCP | H26003-MT-HA0003-H1HPT-MAF001-MEC-P-00-A-PT101-A05-0001 Rev.04 | VR00724_FITP Rev.04 | Code 1 By RIL
3 | Drawing(s) | H26003-MT-HA0003-H1HPT-MAF001-MEC-P-00-A-PT101-B02-0001 Rev.06 | VR00724/Pos.01 (1142354) Rev.05 | Code 1 by RIL
4 | Procedure(s) | PMI procedure: H26003-MT-HA0003-H1HPT-MAF001-MEC-P-00-A-PT101-K07-0001 Rev 02, NDE Procedure:H26003- MT-HA0003-H1HPT-MAF001-MEC-P-00-A-PT101-J02-0001 Rev 02 Weld Procedure: H26003-MT-HA0003-H1HPT-MAF001-MEC-P-00-A-PT101-J01-0001 Rev 02 Painting Procedure: H26003-MT-HA0003-H1HPT-MAF001-MEC-P-00-A-PT101-J04-0001 Rev 04 MRT & PT Procedure: H26003-MT-HA0003-H1HPT-MAF001-MEC-P-00-A-PT101-K01-0001 Rev 05 Leak Test Procedure : H26003-MT-HA0003-H1HPT-MAF001-MEC-P-00-A-PT101-K02-0001 Rev.04 Rotor Balancing Procedure : H26003-MT-HA0003-H1HPT-MAF001-MEC-P-00-PT101-J02-0002 Rev. Packing Procedure : H26003-MT-HA0003-H1HPT-MAF001-MEC-P-00-A-PT101-M02-0001 Rev. 00 | NIL | All procedures in Code.01 By RIL, Packing Procedure Code-04 by RIL and Rotor Balancing Procedure CRS approved by RIL Mail Dt: 25.05.2021.
5 | Datasheet(s) | H26003-MT-HA0003-H1HPT-MAF001-MEC-P-00-A-PT101-D01-0001 Rev.03 | NIL | Code 1 by RIL
6 | Others (Specify) | NIL | NIL | NIL

## Stages Witnessed
Stages Witnessed
ITP Sl No.: 2 - Pre - Inspection meeting attended along with Boldrocchi representative and RIL representative Via TEAMS meeting For OFF Gas Blower.
ITP Sl No.: 4.1 (B) - Random witnessed 10% DP test done on casing, Inlet transition pieces and outlet transition pieces for OFF Gas Blower - No recordable indications were observed.
ITP Sl No.: 4.1 (C) - Random witnessed PMI Test with carbon content in accessible areas for the offered Casing, Inlet cone, Transition piece, Evase, Drain pipe, Fittings and casing weld joints as per ITP and Procedure - Test result meets the relevant material specification and PMI procedure.
ITP Sl No.: 4.2 (B) - Witnessed Check for Coplanar mounting pad surfaces of Base plate for OFF Gas Blower, Tag number : C1-540 - Found satisfactory.
ITP Sl No.: 4.3 (B) - Witnessed random 10% DP test on fillet weld of fabricated Impeller for (TAG NO.C1-540 & TAG NO.C2-540) - No recordable indications were observed.
ITP Sl No.: 4.3 (C) - Random witnessed PMI Test with carbon content in accessible areas for offered Impeller and Hub as per ITP and Procedure - Test result meets the relevant material specification and PMI procedure.
ITP Sl No.: 4.5 (B) - Witnessed dynamic/static balancing carried out on entire offered fabricated Impeller of OFF Gas Blower – Found acceptable with respect to balancing procedure.
ITP Sl No.: 4.7 - Random witnessed PMI Test done on offered Flanges, Fasteners and valves as per ITP and Procedure - Test result meets the relevant material specification and PMI procedure.
ITP Sl No.: 5.7 - Witnessed Chemical Analysis and Rockwell Hardness check on Fasteners (Bolt, Nut & Washers) in NABL Lab - Test result meets the relevant material specification and drawing.
ITP Sl No.: 5.10 - For Motor witnessed refer TUV IRN No : IRN-8116951219-001-Rev.0 Dt: 27.09.2021.
ITP Sl No.: 6.1 - Hydro test for inlet/outlet transition piece along with Casing on offered Off Gas Blower @ 10.5 Bar (TAG NO.C1-540 & C2-540) for 60 minutes with rubber gasket 3 mm thick on sealing faces – Found no leak observed
ITP Sl No.: 6.2 - Witnessed Performance test as per approved procedure and AMCA 210 at rated speed with job motor and measured the RPM, absorbed power, Capacity, pressure & Efficiency for the offered OFF Gas Blower, TAG NO.C2-540 - Found acceptable and reports attested for records.
ITP Sl No.: 6.3 & Note.5 - Witnessed Mechanical run test was carried out with Job motor for ATM. Absorber Off Gas Blower, Tag No: C1-540 & C2-540 and On Spare Rotor, duration of 4hours following parameter checked RPM, Current, Voltage, bearing temperature, Vibration and noise level – Result with respect to procedure found acceptable and report attested for records.
ITP Sl No.: 6.4 - Witnessed soap bubble leak test during MRT for ATM. Absorber Off Gas Blower, Tag No: C1-540 & C2-540 and On Spare Rotor - Found no leak observed on welding and gasket joints.and report attested for records.
ITP Sl No.: 6.5 - Witnessed Visual Examination and Paint DFT check at random spot carried out on offered Base Frame – Observed Micron are within 250 micron to 300 micron and for Impeller / Inlet Cone - Observed Micron are within 75 micron to 120 micron and For Casing with inlet box, Inlet & outlet Transition for Tag No.C1-540 & Tag No.C2-540 with respect to approved procedure – Observed Micron are within 210 micron to 250 micron.
ITP Sl No..6.5 - Witnessed Adhesion test (X- Cut) at random spot carried out on offered Base Frame and Casing with inlet box for Tag No.C1-540 & Tag No.C2-540 with respect to approved procedure – Found acceptable as per ASTM D3359 Observed Level-01.
ITP Sl No..6.5 - Witnessed Paint Shade verification done on offered Base Frame for Tag No.C1-540 & Tag No.C2-540 with respect to IS631 – Found Satisfactory.
ITP Sl No.. 6.6 - Witnessed Visual Examination and Final dimensional check (In Assembled condition) carried out for OFF Gas Blower with base frame assembly (Overall dimension, TP Point verification and name Plate verification) - Found Within acceptable tolerance with respect to approved Drawing.
ITP Sl No..6.8 - Physically Verified supply limit check for main supply and spares as per spare list - Found acceptable and reports attested for records.

## Document reviewed
Document reviewed
ITP Sl No.: 1.1 to 1.9 - Verified the RIL approved document (Welding procedure, NDE Procedure, Rotor Balancing Procedure, Painting and pickling procedure, MRT/PT Procedure, PMI Procedure, Hydrotest Procedure, Packing and preservation procedure) - Found in order.
ITP Sl No.: 3.1 - Reviewed Photocopy of Manufcaturer test certificate and NABL Lab Test report for IGC - Practice- E for Impeller (Center Plate, Blades, Front Plates), Hub and Lock Plate - Found to meet the material Specification and Approved Drawing.
ITP Sl No.: 3.2 - Reviewed Photocopy of Manufcaturer test certificate for Forged Shaft - Found to meet the material Specification and Approved Drawing.
ITP Sl No.: 3.3 - Reviewed Photocopy of Manufcaturer test certificate and NABL Lab Test report for IGC - Practice- E for Casing, Inlet Cone, Inlet & Outlet Transition Piece - Found to meet the material Specification and Approved Drawing.
ITP Sl No.: 3.4 - Reviewed Photocopy of Manufcaturer test certificate Pedestal and baseframe - Found to meet the material Specification and Approved Drawing.
ITP Sl No.: 3.5 - Reviewed Photocopy of Manufcaturer test certificate for Shaft sleeve - Found to meet the material Specification and Approved Drawing.
ITP Sl No.: 4.1 (A) - Reviewed Radiographic Test report/Films for casing Butt weld Joint - No Relevant indication were noticed.
ITP Sl No.: 4.2 (A) - Reviewed DPT Report of Lifting lug for Pedestal and baseframe - Found in order.
ITP Sl No.: 4.2 (B) - Reviewed Check for Coplanar mounting pad surfaces of Base plate for OFF Gas Blower, Tag number : C2-540 - Found in order.
ITP Sl No.: 4.3 (A) & (D) - Reviewed Radiographic Test report/Films for Impeller Butt weld Joint - No Relevant indication were noticed and Reviewed Dimension Report for Impeller & Hub - Found in order.
ITP Sl No.: 4.4 - Reviewed Shaft (UT report, Run Out Check report, LPT report, PMI report, Dimension report) - Found in order.
ITP Sl No.: 4.5 (A) - Reviewed Visual and Dimension report for Fabricated Rotor - Found in order.
ITP Sl No.: 5.1, 5.2, 5.3 & 5.4 - Reviewed Bought out item test certificates for Bearing housing, Bearing, shaft Seals & Coupling (Balancing Report & Warranty Certificate) - Found in order and attested for records.
ITP Sl No.: 5.5 - Reviewed Test certificates for Transmitters, RTD, Vibration sensor, Junction box and LCP and Verified Statutory Certificate for Junction box and LCP -Found in order.
ITP Sl No.: 5.6 & 5.9 - Reviewed Bought out item Compliance certificates for Tubing/Fittings And Coupling guard - Found in order.
ITP Sl No.: 5.8 - Reviewed Filler wire Batch cerificate used for OFF Gas Blower - Found in order.
ITP Sl No.: 5.10 - For Motor Review document refer TUV IRN No : IRN-8116951219-001-Rev.0 Dt: 27.09.2021.
ITP Sl No.: 6.7 - Reviewed Packing List for OFF Gas Blower Tag No : C1 540 & C2 540 - Found in order.

## Details of measuring instrument
Sr. No. | Detail of Equipment(s) / Instrument(s) | Range | ID | Validity till Date | Calibration Certificate Number | NABL / OTHER CERT. BODIES / NABL Traceability (type Yes wherever applicable) | NON-NABL (type Yes wherever applicable)
1 | Pressure Gauge | 0 to 21Kg/cm2 | 744 | 30.12.2022 | 2021-22/ CFC/ 2286 1 date: 30.12.2021 | yes |  | Yes
1 | Vibration Meter | 0.5 to 200 mm/s | S011789 | 10.09.2022 | E210911-1-1 | YES |  | No
2 | IR | 60 TO 625°C | 1103223 | 20.08.2022 | PC-18-21/ATL/3164-05 | YES
3 | Measuring Tape | 0 to 5 mtrs | BI/QC/D/07 | 09.07.2022 | GTO 102.02/21-22
4 | Tachometer | 5 to 99999rpm | Q 643285 | 08.07.2022 | PC-07-21/ATL/2410-01 | YES
5 | Sound Level Meter | 35 to 130DB | Q-636930 | 28.01.2023 | E290122-2-1 | YES

## Areas of concerns
Areas Of Concern

## Pending Activities
Pending Activities from this visit
As per Approved QAP, Vendor shall offer the balance activities to TUV for Witness / Review as applicable.

## Conclusion
Note: Data filled in this sheet will not upload in TIIMES
Non Conformities raised / Discrepancies observed during Inspection (If Any, Mention TUV India NCR Number ):
NIL
Identification of Inspected Item(s):
Not Applicable
Conclusion (Acceptable / Not Acceptable / Acceptance subject to):
NDT DP test acceptable ,Hydrotest result subject to client acceptance for testing with rubber gaskets.
IRN can be issued for PO Item numbers:
Expenses:
Remarks: