## Notes
Notes:
Data filled in General and conclusion Sections will not upload in TIIMES. Please use these sections to keep data ready for copy paste.
Data in Item Description columns of Accepted Quantity and cumulative Accepted quantity must be verified thoroughly before uploading in TIIMES.
Pending activity, Areas of concern & Details of measuring instruments sheets are applicable for IVR.
Select options from drop down list for unit of measurement (Item Description) & certifying body of measuring instruments (Details of measuring instruments).
Do not modify this format.
To start next row in cell itself use below shortcut: press 'alt + Enter' keys together. Alt + Enter

## General
Note: - Data filled in this sheet will not upload in TIIMES
Title | Details
Control Number
SAP number
Notification Number
Project Name & Location
Client Name
End User Name
DEC / PMC / EPC Name
DEC / PMC / EPC Number
Vendor Name
PO Number (Client PO on Vendor)
Sub Vendor
PO Number (Vendor PO on Sub Vendor)
Inspection Location
Inspection Date(s)

## Item Description
Po Item No. | Item Code | Item Description | Unit | Po Quantity | Offered Quantity | Accepted Quantity (Please verify thouroghly before using this Column for IRN) | Cumulative Accepted Quanitity (for IRN Only)
1 | -- | BEM Type Heat Exchanger Tag no : E-165,Mfr.Sr.no : H-2613 | each | 1 | 1 | 1 | 1 | number
meter
km
meter (number)
km (number)
each
Piece
Test sample
AU - All Unit
lot
Set
Running Meter
kg
metric ton (tonne)
ton
cubic millimetre
cubic centimeter
cubic meter
cubic inch
cubic foot
mm
cm
in
foot
mile
yard
liter
kl
cl
ml
g
lb
oz
Sq. mm
Sq. cm
Sq. meter
Sq. in
Sq. foot

## Reference Documents
Sr. No. | Document Name | Client Document Number | Vendor Document Number | Approval Status
1 | PR/MR/ARM | MT-P20P02-D1PPT-MBC003-MEC-Q-00 | Not Applicable | Provided by RIL
2 | QAP/ITP/QCP | MT-P20P02-D1PPT-MBC003-LTH-P-00-A-PT401-A05-0003 Rev.02 | INTO1002-0810 Rev.02 | Approved with commnets in Code -1 By RIL & LTHE & KES
3 | Drawing(s) | MT-P20P02-D1PPT-MBC003-LTH-P-00-A-PT401-B02-0003 Rev.03 MT-P20P02-D1PPT-MBC003-LTH-P-00-A-PT401-F01-0015 Rev.03 'MT-P20P02-D1PPT-MBC003-LTH-P-00-A-PT401-F01-0045 Rev.03 'MT-P20P02-D1PPT-MBC003-LTH-P-00-A-PT401-F01-0005 Rev.03 | INTO1002-0270 Rev.03 sheet 1 of 4 INTO1002-0710 Rev.03 sheet 2 of 4 INTO1002-3320 Rev.03 sheet 3 of 4 INTO1002-0610 Rev.03 sheet 4 of 4 | Approved with commnets in Code -1 By LTHE & KES
4 | Procedure(s) | Welding book: MT-P20P02-D1PPT-MBC003-LTH-P-00-A-PT401-J01-0002 Rev.03 NDE Procedure: MT-P20P02-D1PPT-MBC003-LTH-P-00-A-PT401-J02-0002 Rev.01 Hydro test procedure: MT-P20P02-D1PPT-MBC003-LTH-P-00-A-PT401-K02-0002 Rev.02 Hardness test procedure: MT-P20P02-D1PPT-MBC003-LTH-P-00-A-PT401-K03-0002 Rev.01 Ferrite procedure: MT-P20P02-D1PPT-MBC003-LTH-P-00-A-PT401-K01-0009 Rev.02 Pneumatic test procedure: MT-P20P02-D1PPT-MBC003-LTH-P-00-A-PT401-K02-0012 Rev.01 PMI Procedure: MT-P20P02-D1PPT-MBC003-LTH-P-00-A-PT401-K07-0002 Rev.01 Painting procedure: MT-P20P02-D1PPT-MBC003-LTH-P-00-A-PT401-J04-0003 Rev.00 Packing shipping,marking procedure: MT-P20P02-D1PPT-MBC003-LTH-P-00-A-PT401-M02-0002 Rev.01 | AEL/WPS-PQR/H-2613 Rev.03 INTO1002-1160 Rev.01 INTO1002-0980 Rev.02 INTO1002-2160 Rev.01 INTO1002-3360 Rev.02 INTO1002-1330 Rev.01 INTO1002-1960 Rev.01 INTO1002-1860 Rev.00 INTO1002-1240 Rev.01 | Approved in Code -1 By LTHE & KES
5 | Datasheet(s) | Not Applicable | Not Applicable | Not Applicable
6 | Others (Specify) | Not Applicable | Not Applicable | Not Applicable

## Stages Witnessed
Stages Witnessed
ITP stage no. 3.1 to 3.5 Witnessed Material identification of pressure parts & Bought out items as per ITP requirements-Found acceptable.
ITP stage no. 3.6 Visual & dimension inspection carried out of Em Baffle in as received condition-Found acceptable.
ITP Stage no: 3.8 -Visual & dimension inspection carried out of thermal block-found acceptable.
ITP Stage no: 4.1 -Visual & dimension inspection carried out of Top & bottom cone-found acceptable.
ITP Stage no: 4.2 -PT examination carried out of WEP & long seam of top & Bottom cone from both side-No relavent indication observed -found acceptable.
ITP Stage no: 5.1 -Witnessd long seam set up of Main shell,Vapour shell ,Inner sleeve,Top & bottom channel shell at random -found acceptable.
ITP Stage no: 5.2 -Witnessd cir seam set up of Main shell to Main shell,Main shell to Vapour shell,Vapour belt cone ,Vapour belt shell to Tube sheet,channel shell to cone & girth flange -found acceptable.
ITP Stage no: 5.5 -Witnessd Nozzle to Branch nozzle ,Nozzle shell ,Nozzle to tube sheet & Nozzle to channel cone set up at random-found acceptable.
ITP Stage no: 6.3 -PT Examination carried out of all weld of main shell,top & Bottom channle shell assembly from inside & outside-No relavent indication observed -found acceptable. -Reviewed RT fillms of butt weld joints \as per approved weld map-found acceptable.
ITP Stage no: 7.2 Visual & Dimension inspection carried out of top & Bottom Tube sheet after machining & drilling-found acceptable.
ITP stage no.7.4 Visual & Dimension inspection carried out of Skeleton assembly before tube insertion-found acceptable.
ITP Stage no: 7.5 Visual & Dimension inspection carried out of Tube bundle assembly after Tube insertion-found acceptable.
ITP Stage no: 7.6 Witnessed tube bundle insertion & withdrawal for Approx.1220 mm distance -After insertion & withdrawal visual inspection carried out of bundle & main shell from inside Smooth insertion & no abnormal noise observed during insertion-found satisfactory.
ITP Stage no: 7.8 -Visual Examination carried out of TTJ final run weld for both side before Expansion-found satisfactory. -PT Examination carried out of TTJ final run weld for both side before Expansion-No relavent indication observed -found acceptable.
ITP Stage no: 7.9 Witnessed Pneumatic test for tube to tube sheet Joint at pressure 1.25 kg/cm2(g) before Expansion - neither leakage nor bubble formation observed during testing.-found acceptable.
ITP Stage no: 7.10 Witnessed expansion for 25% Randomly selected tube to tube sheet joint after expansion- Found acceptable
ITP Stage no: 7.11 -Visual Examination carried out of TTJ final run weld for both side after Expansion-found satisfactory. -PT Examination carried out of TTJ final run weld for both side after Expansion-No relavent indication observed -found acceptable.
ITP Stage no: 8.1 -Visual & Dimension inspection carried out of Vapour cone & shell assembly before inner sleeve set up-found acceptable.
ITP Stage no: 8.2 Witnessed RF Pad Pneumatic test of Main shell & Channel shell Nozzle from inside & outside at pressure 1.5 kg/cm2(g) - neither leakage nor bubble formation observed during testing.
ITP Stage no: 8.3 Visual inspection carried out of inside surface of Main shell assembly before insertion of Tube bundle -Found satisfactory.
ITP Stage no: 8.4 Witnessed Pull through gauge passing inside of main shell assembly. Verified dimension of Pull through gauge-Found acceptable
ITP Stage no: 8.5 Visual inspection carried out of inside surface of Main shell assembly after pickling & passivation -Found satisfactory.
ITP Stage no: 8.6 Final Internal & External Visual & Dimension inspection carried out of Main shell assembly before Hydro test -Found acceptable.
ITP Stage no: 8.7 Final Internal & External Visual & Dimension inspection carried out of Top & bottom channel shell assembly before Hydro test -Found acceptable.
ITP Stage no: 8.8 Checked hardness of Butt weld,HAZ & base metal of Main shell ,Top & bottom channel shell assembly from inside & outside at random -Found less than 241 BHN.
ITP Stage no: 8.9 Ferrite Examination carried out of Main shell ,Top & bottom channel shell assembly weld joint from inside & outside at random -Found between 3 to 10 FN.
ITP Stage no: 8.10 PMI Examination carried out of all SS component & weld of Main shell ,Top & bottom channel shell assembly at random-Element found to meet the specification requirements.
ITP Stage no: 9.1 Witnessed final shell side hydrostatic test at pressure 62 kg/cm2(g) in horizental condition for holding time 1 hour-Neither leakage nor pressure drop observed during holding time.
ITP Stage no: 9.2 Visual inspection carried out of TTJ joint & Top ,Bottom tube sheet after pickling & passivation before tube side hydro test-Found satisfactory.
ITP Stage no: 9.3 Witnessed final tube side hydrostatic test along with Top & bottom channle shell assembly at pressure 48 kg/cm2(g) in horizental condition for holding time 1 hour-Neither leakage nor pressure drop observed during holding time.
ITP Stage no: 10.1 Witnessed draining & drying for shell side & tube side after 48 hours of hydrostatic test.Visual check from Nozzle accessible area.also Verified humidity for shell side & tube side-foundsatisfactory.
ITP Stage no: 10.2 Visual inspection carried out of complete equipment from outside after pickling & passivation-Found satisfactory.
ITP Stage no: 10.4 -Visual inspection carried out of Top support plate ( qty -04 Nos.) after finished paint-found satisfactory. -Checked DFT of Top support plate ( qty -04 Nos.) after finished paint-found as per painting procedure requirements. -Witnessed ahhesion test ,Verified shade & RAL number -foudn acceptable.
ITP Stage no: 10.5 Verified spare as per Approved drawing requirements-found acceptable.
ITP Stage no: 10.6 Verified Name plate & Rubb.off detail on equipment-found acceptable.
ITP Stage no: 10.7 - Witnessed N2 purging at pressure 0.5 kg/cm2 (g) in Exhaust nozzle of shell side & tube side after 24 hours. Verified bolting Joints with soap solution-Neither leakage nor bubble formation observed. Found acceptable. - Checked Oxygen content in Exhaust nozzle of shell side & tube side after 24 hours -Found ˂ 1%
ITP Stage no. 10.8 Witnessed Packing & marking of complete Equipment as per packing procedure requirements-found acceptable.

## Document reviewed
Document reviewed
ITP stage no: 1.3 Reviewed WPS/PQR along with weld map - Found in order.
ITP stage no: 1.4 Reviewed TTJ mock up as per section IX requirements- Found in order.
ITP stage no: 1.5 Reviewed welder certificate & Expansion operator - Found in order.
ITP stage no: 1.6 Reviewed NDE Personnel qualification certificate - Found in order.
ITP stage no: 1.7 Reviewed Job procedures as per approved ITP - Found in order.
ITP stage no: 3.1 to 3.5 Reviewed Material heat chart for pressure parts, Direct attached to pressure parts along with Material test certificate - Found to meet material specification requirements.
ITP stage no: 3.7 Reviewed Material heat chart for Non-pressure parts along with Material test certificate - Found to meet material specification requirements.
ITP stage no: 3.8 Reviewed PMI Examination report of receipt material - Found in order.
ITP stage no: 4.2 Reviewed RT Films for Top & bottom cone butt weld joints - Found acceptable.
ITP stage no: 5.3 Reviewed Set up report for pipe to WNRF Flange - Found acceptable.
ITP stage no: 6.1 Reviewed weld consumable test certificate – Found in order.
ITP stage no: 6.2 Reviewed PT Examination report of WEP & Back chip/Root Run as per ITP requirements-Found in order.
ITP stage no: 6.3 Reviewed RT films for butt weld Joints & RT Summery -found acceptable.
ITP Stage no: 7.7 -Visual & PT Examination report of TTJ root run weld for both side-found in order.
Reviewed Water chloride content test report-Found in order.
ITP stage no: 10.3 Reviewed Surface preparation & painting inspection report for Top support plate-Found in order.
ITP stage no: 10.9 Reviewed Documents as per approved ITP-Found in order.

## Details of measuring instrument
Sr. No. | Detail of Equipment(s) / Instrument(s) | Range | ID | Validity till Date | Calibration Certificate Number | NABL / OTHER CERT. BODIES / NABL Traceability (type Yes wherever applicable) | NON-NABL (type Yes wherever applicable)
1 | Ultrasonic thickness gauge | 2.0 to 200mm | UTG-02 | 24.12.2022 | Paramount/64200 Dated 25.12.2021 |  | Yes | Yes
2 | Measuring Tape | 0-5000 mm | MT-10 | 28.12.2022 | Paramount/64279 Dated 29.12.2021 |  | Yes | No
3 | Measuring Tape | 0-15000 mm | MT-21 | 28.12.2022 | Paramount/64290 Dated 29.12.2021 |  | Yes
4 | Vernier calliper | 0-300 mm | LVC 0402 | 30.08.2022 | Paramount/60825 dated 31.08.2021 |  | Yes
5 | Ferritescope meter | 100% | 100020931 | 11.12.2022 | Paramount/64106 dated 12.12.2021 |  | Yes
6 | Portable hardness tester | -- | E210407316000 | 17.02.2023 | Paramount/658020 dated 18.02.2022 |  | Yes

## Areas of concerns
Areas Of Concern
none.

## Pending Activities
Pending Activities from this visit
NONE.

## Conclusion
Note: Data filled in this sheet will not upload in TIIMES
Non Conformities raised / Discrepancies observed during Inspection (If Any, Mention TUV India NCR Number ):
Identification of Inspected Item(s):
Conclusion (Acceptable / Not Acceptable / Acceptance subject to):
IRN can be issued for PO Item numbers:
Expenses:
Remarks: