## Notes
Notes:
Data filled in General and conclusion Sections will not upload in TIIMES. Please use these sections to keep data ready for copy paste.
Data in Item Description columns of Accepted Quantity and cumulative Accepted quantity must be verified thoroughly before uploading in TIIMES.
Pending activity, Areas of concern & Details of measuring instruments sheets are applicable for IVR.
Select options from drop down list for unit of measurement (Item Description) & certifying body of measuring instruments (Details of measuring instruments).
Do not modify this format.
To start next row in cell itself use below shortcut: press 'alt + Enter' keys together. Alt + Enter

## General
Note: - Data filled in this sheet will not upload in TIIMES
Title | Details
Control Number
SAP number
Notification Number
Project Name & Location
Client Name
End User Name
DEC / PMC / EPC Name
DEC / PMC / EPC Number
Vendor Name
PO Number (Client PO on Vendor)
Sub Vendor
PO Number (Vendor PO on Sub Vendor)
Inspection Location
Inspection Date(s)

## Item Description
Po Item No. | Item Code | Item Description | Unit | Po Quantity | Offered Quantity | Accepted Quantity (Please verify thouroghly before using this Column for IRN) | Cumulative Accepted Quanitity (for IRN Only)
10 | CH000116395 | HORIZ HEAT EXCH GPH Vent Condenser Heating Surface area : 51.38 M2 GRF-6 / Dia 10 / 7 Blocks Process Side - 1 Pass, Service Side - 2 Pass / Blk. Equipment Sr No. is - ES-8490/22 Tag No - 7-HE016-C-105 | number | 1 | 1 | 1 | 1 | number
30 | CH000105181 | CYL POLYBLK HEAT EXCH GPH ODCB Heat Interchanger Heating Surface area : 37.32 M2 GRF-4 / Dia 8 / 12 Blocks Process Side - 7 Pass, Service Side - 5 Pass / Blk. Equipment Sr No. is - ES-8492/22 Tag No - 7-HE026 | number | 1 | 1 | 1 | 1 | meter
40 | CH000105182 | CYL POLYBLK HEAT EXCH GPH Column ODCB Chiller Heating Surface area : 37.32 M2 GRF-4 / Dia 8 / 12 Blocks Process Side - 7 Pass, Service Side - 2 Pass / Blk. Equipment Sr No. is - ES-8493/22 Tag No - 7-HE033-C1 | number | 1 | 1 | 1 | 1 | km
meter (number)
km (number)
each
Piece
Test sample
AU - All Unit
lot
Set
Running Meter
kg
metric ton (tonne)
ton
cubic millimetre
cubic centimeter
cubic meter
cubic inch
cubic foot
mm
cm
in
foot
mile
yard
liter
kl
cl
ml
g
lb
oz
Sq. mm
Sq. cm
Sq. meter
Sq. in
Sq. foot

## Reference Documents
Sr. No. | Document Name | Client Document Number | Vendor Document Number | Approval Status
1 | PR/MR/ARM | Not Applicable | Not Applicable | Not Applicable
2 | QAP/ITP/QCP | Not Applicable | GIL/QAP/1120672/01 Rev - 00 | Approved by Aarti Industries Ltd.
3 | Drawing(s) | Not Applicable | GV/35699/22 Rev - 0 GV/35701/22 Rev - 1 GV/35702/22 Rev - 1 | Approved by Aarti Industries Ltd.
4 | Procedure(s) | Not Applicable | Not Applicable | Not Applicable
5 | Datasheet(s) | Not Applicable | Not Applicable | Not Applicable
6 | Others (Specify) | Not Applicable | Not Applicable | Not Applicable

## Stages Witnessed
Stages Witnessed
As per QAP Clause No - 4 C. (a & b)
i) Visual Inspection for Graphite Equipment in primer painted condition (PO Sr No. 10 only) for outer surface & for internal surface upto visible area carried out. ii) No surface defects oberved at the time of inspection. iii) Workmanship Found Satisfactory.
i) Dimensional Inspection of Graphite Equipment Witnessed. ii) Dimensions for total length, ODCF, height, Nozzle projections, Elevation, Nozzle size witnessed - found as per drawing & within given tolerance (For out of tolerance dimension vendor has received client acceptance email dated - 07.04.2023). iii) Dimensions for Equipment Mouting / Foundation details (i.e C/C Distance, Hole Dia, Slot Size, base plate size etc) witnessed - found as per drawing. iv) Other dimensions mentioned in drawing witnessed - found as per drawing & with in tolerance.
i) Graphite Equipments Process side Hydro test witnessed at a pressure 5.2 kg/cm2 (For PO Sr No 10 & 30) & 6.5 kg/cm2 (For PO Sr No 40) for a pressure holding period of 30 minutes (minimum) as mentioned in the drawing - No leakages / No pressure drop observed during pressure holding time – Test found Satisfactory. ii) Graphite Equipments Service side Hydro test witnessed at a pressure 5.2 kg/cm2 (For PO Sr No 10 & 30) & 6.5 kg/cm2 (For PO Sr No 40) for a pressure holding period of 30 minutes (minimum) as mentioned in the drawing - No leakages / No pressure drop observed during pressure holding time – Test found Satisfactory. iii) Graphite equipment is in primer painted condition (PO Sr No - 10 only) at the time of hydrotest excpet weld joints.

## Document reviewed
Document reviewed
As per QAP Clause No - A-1 : Vendor's Declaration certificate for PTFE / Phenolic Impregnated Graphite block properties as provided by vendor reviewed - Found in order.
As per QAP Clause No - A-2 & 3 : Vendor's Declaration certificate for visual, dimensions & Imperviousness testing of PTFE / Phenolic Impregnated Graphite block as provided by vendor reviewed - Found in order.
As per QAP Clause No - B-1 & 3 : Vendor's declaration certificate for material used for fabricated item & workmanship (visual , dimensional & pressure test) of fabricated items as provided by vendor reviewed - found in order.
For PO Sr No - 30 (Tag No - 7 - HE026 , As per QAP Clause No - C - a : Manufacturers Test certificate for PFA resin as provided by vendor reviewed - found in order. As per QAP Clause No - C - b to g : Vendor's internal inspection report for Visual , Dimensional , Spart Test (before & after pressure test), Pneumatic Test & Hydro static test of PFA lined shell as provided by vendor reviewed - found in order.
Calibration certificate of measuring instruments used for inspection are reviewed - found in order.

## Details of measuring instrument
Sr. No. | Detail of Equipment(s) / Instrument(s) | Range | ID | Validity till Date | Calibration Certificate Number | NABL / OTHER CERT. BODIES / NABL Traceability (type Yes wherever applicable) | NON-NABL (type Yes wherever applicable)
1 | Measuring Tape | 0 - 5 Mtr | MT - 02 | 11.10.2023 | 2022/10/1179 Date : 12.10.2022 | Yes |  | Yes
2 | Pressure Gauge | 0 - 25 Kg/cm2 | GV-M-12 | 02.03.2024 | MI/MCH/0813/01/2022-23 Date : 04.03.2023 | Yes |  | No
3 | Vernier Calliper | 0 - 300 mm | GV-143 | 22.04.2023 | SSPi&RC/202204878 Date : 22.04.2022 |  | Yes
4 | Pressure Guage | 0 - 16 kg/cm2 | GV - 398 | 20.04.2023 | GV - 398 Date : 20.03.2023 |  | Yes
5 | Pressure Guage | 0 - 16 kg/cm2 | GV - 378 | 20.04.2023 | GV - 378 Date : 20.03.2023 |  | Yes
6 | Pressure Guage | 0 - 16 kg/cm2 | GV - 361 | 10.04.2023 | GV - 361 Date : 10.03.2023 |  | Yes
7 | Pressure Guage | 0 - 16 kg/cm2 | GV - 360 | 10.04.2023 | GV - 360 Date : 10.03.2023 |  | Yes
8 | Pressure Guage | 0 - 10 kg/cm2 | GV - 14 | 20.04.2023 | GV - 14 Date : 20.03.2023 |  | Yes
9 | Pressure Guage | 0 - 16 kg/cm2 | GV - 25 | 20.04.2023 | GV - 25 Date : 20.03.2023 |  | Yes
10 | Measuring Tape | 0 - 15 Mtr | MT - 03 | 11.10.2023 | 2022/10/1180 Date : 12.10.2022 | Yes
11 | Ultrasonic Thickness Gauge | 0.75 to 300 mm | UTG - 01 | 17.10.2023 | 22/1301 Date : 18.10.2022 | Yes

## Areas of concerns
Areas Of Concern
For PO Sr No - 10 (Tag No - 7 - HE016-C-105) a) Insulation cleat arrangment not shown in GAD , at actual vendor has provided insulation cleat at two location circumferentially.
For PO Sr No - 30 (Tag No - 7 - HE026) a) PCD for Nozzle N7 & N8 , required as per drawing is 79.4 mm , actual observed is 70 mm.
For PO Sr No - 40 (Tag No - 7-HE033-C1) a) Elevation for nozzle N5 required as per drawing is 400 mm from N2 Nozzle Face , actual observed is 390 mm. b) Elevation for nozzle N7 required as per drawing is 375 mm from N2 Nozzle Face , actual observed is 365 mm. c) Elevation for mounting frame required as per drawing is 800 mm from N2 Nozzle Face , actual observed is 790 mm.

## Pending Activities
Pending Activities from this visit
None

## Conclusion
Note: Data filled in this sheet will not upload in TIIMES
Non Conformities raised / Discrepancies observed during Inspection (If Any, Mention TUV India NCR Number ):
Identification of Inspected Item(s):
Conclusion (Acceptable / Not Acceptable / Acceptance subject to):
IRN can be issued for PO Item numbers:
Expenses:
Remarks: