## Notes
Notes:
Data filled in General and conclusion Sections will not upload in TIIMES. Please use these sections to keep data ready for copy paste.
Data in Item Description columns of Accepted Quantity and cumulative Accepted quantity must be verified thoroughly before uploading in TIIMES.
Pending activity, Areas of concern & Details of measuring instruments sheets are applicable for IVR.
Select options from drop down list for unit of measurement (Item Description) & certifying body of measuring instruments (Details of measuring instruments).
Do not modify this format.
To start next row in cell itself use below shortcut: press 'alt + Enter' keys together. Alt + Enter

## General
Note: - Data filled in this sheet will not upload in TIIMES
Title | Details
Control Number
SAP number
Notification Number
Project Name & Location
Client Name
End User Name
DEC / PMC / EPC Name
DEC / PMC / EPC Number
Vendor Name
PO Number (Client PO on Vendor)
Sub Vendor
PO Number (Vendor PO on Sub Vendor)
Inspection Location
Inspection Date(s)

## Item Description
Po Item No. | Item Code | Item Description | Unit | Po Quantity | Offered Quantity | Accepted Quantity (Please verify thouroghly before using this Column for IRN) | Cumulative Accepted Quanitity (for IRN Only)
1 | TS-12003/12005 | STORAGE TANK 20KL | number | 3 | 2 | 2 | 2 | number
meter
km
meter (number)
km (number)
each
Piece
Test sample
AU - All Unit
lot
Set
Running Meter
kg
metric ton (tonne)
ton
cubic millimetre
cubic centimeter
cubic meter
cubic inch
cubic foot
mm
cm
in
foot
mile
yard
liter
kl
cl
ml
g
lb
oz
Sq. mm
Sq. cm
Sq. meter
Sq. in
Sq. foot

## Reference Documents
Sr. No. | Document Name | Client Document Number | Vendor Document Number | Approval Status
1 | PR/MR/ARM | Not Applicable | Not Applicable | Not Applicable
2 | QAP/ITP/QCP | Not Applicable | SIL/Standard_QAP/02 Rev 00 | Approved By UPL
3 | Drawing(s) | Not Applicable | SIL/2023-24/20VJR/W-7064-7066/01 Rev 01 | Approved By UPL
4 | Procedure(s) | Not Applicable | Not Applicable | Not Applicable
5 | Datasheet(s) | Not Applicable | Not Applicable | Not Applicable
6 | Others (Specify) | Not Applicable | Not Applicable | Not Applicable

## Stages Witnessed
Stages Witnessed
QAP Clause No 8.1 - Witnessed Hydro Test for Main Shell & Jacketed shell as per Pressure given in un approved drawing and QAP requirements (6Kg/cm2) for 30 Min Minimum Holding times - No leakage and no pressure drop Observed during more than 30 Minutes holding time. Found Satisfactory.
QAP Clause No 8.2 - Witnessed Spark Test @ 11 KV as per drawing and QAP requirements - No Spark at 11 KV hence found Satisfactory.
QAP Clause No 8.2 - Witnessed Glass Lining Thickness on random location with Digital coating thickness gauge as per QAP requirements & results found to meet the requirements. Found Satisfactory.
QAP Clause No: - 9.1 witnessed Dimensions as per Approved Drawing and refer area of concern for same.
QAP Clause No: - 9.1 Visual Inspection Carried out for surface finish and result found no any surface defect or any dent observed during inspection time hence found satisfactory.
All measuring instruments/ equipment were verified for continued suitability for intended use, proper identification, calibration status, traceability to national standards & found satisfactory.

## Document reviewed
Document reviewed
QAP Clause No: - 1.1 & 1.2 Reviewed Raw Material and Bought out item test Certificates for Pressure & Non Pressure Parts as per approved requirements and Found in order.
QAP Clause No: - 2.1 & 2.2 Reviewed Inetrnal Inspeciton Reports as per QAP & found in order.
QAP Clause No: - 3.1 Reviewed Final Dimensions & Visual Inspection Report as per QAP & Found in Order.
QAP Clause No: - 4.1 & 4.2 Reviewed LPT & RT (Weld Joints) Reports as per QAP & Found in Order.
QAP Clause No: - 5.1 Reviewed Surface Inspection Reports as per QAP & Found in Order.
QAP Clause No: - 6.1 Reviewed Surface Finish Glass Lining Thk & Spark Tets Inspection Reports as per QAP & Found in Order.
QAP Clause No: - 7.1 (Jacket Fittings) Reviewed Inetrnal Visual & Dimension Inspection Reports of Finished Weld bead for jacket fittings as per QAP & Found in Order.
Reviewed Materials Heat Chart and found in order.

## Details of measuring instrument
Sr. No. | Detail of Equipment(s) / Instrument(s) | Range | ID | Validity till Date | Calibration Certificate Number | NABL / OTHER CERT. BODIES / NABL Traceability (type Yes wherever applicable) | NON-NABL (type Yes wherever applicable)
1 | Measuring Tape | 0-15000 mm | MT-15-05/ | 13.03.2024 | CC2529230000001099F Dated 16.03.2023 | Yes | No | Yes
2 | Measuring Tape | 0-5000 mm | MT-5-01/ | 13.03.2024 | CC2529230000001101F Dated 16.03.2023 | Yes | No | No
3 | Pressure Gauge | 0-14 KG/Cm2 | MPC-221211J | 07.09.2023 | 1190095 Dated 08.09.2022 | No | Yes
4 | Pressure Gauge | 0-14 KG/Cm2 | MPC-221207J | 07.09.2023 | 1190091 Dated 08.09.2022 | No | Yes
5 | Pressure Gauge | 0-14 KG/Cm2 | MPC-221212J | 07.09.2023 | 1190096 Dated 08.09.2022 | No | Yes
6 | Pressure Gauge | 0-14 KG/Cm2 | MPC-221214J | 07.09.2023 | 1190098 Dated 08.09.2022 | No | Yes
7 | High Voltage Spark Tester | 0-30KV DC | KV-01 | 26.09.2023 | CC252922000005085F Dated 28.09.2022 | Yes | No
8 | Digital Coating Thk Gauge | 0-3000 Micron | F 170833 | 17.03.2024 | BE/18/03/3011 Dated 18.03.2023 | No | Yes

## Areas of concerns
Areas Of Concern
Dimension witnessed on accessible location only.
Dish Circumference OD checked instead of shell OD. Sheel Dimensions could not be checked due to covered by jacket fitting.
Dish Circumference Found 8750 instead of 8800. please confirm.
Please refer Dimension reprots for Nozzle Dimension verication.
M/s Sachin to prepare as build drawing and submit to client for approval. For Information only.
Hydro Test Witnessed in Primier condition. For Your Information only as it is already mentioned in Approved QAP.

## Pending Activities
Pending Activities from this visit
None

## Conclusion
Note: Data filled in this sheet will not upload in TIIMES
Non Conformities raised / Discrepancies observed during Inspection (If Any, Mention TUV India NCR Number ):
Identification of Inspected Item(s):
100% witnessed straight tubes are identified with hard [Single] stamped as “ ”on Metal tags fixed on bundle
Conclusion (Acceptable / Not Acceptable / Acceptance subject to):
IRN can be issued for PO Item numbers:
Expenses:
Remarks: