## Notes
Notes:
Data filled in General and conclusion Sections will not upload in TIIMES. Please use these sections to keep data ready for copy paste.
Data in Item Description columns of Accepted Quantity and cumulative Accepted quantity must be verified thoroughly before uploading in TIIMES.
Pending activity, Areas of concern & Details of measuring instruments sheets are applicable for IVR.
Select options from drop down list for unit of measurement (Item Description) & certifying body of measuring instruments (Details of measuring instruments).
Do not modify this format.
To start next row in cell itself use below shortcut: press 'alt + Enter' keys together. Alt + Enter

## General
Note: - Data filled in this sheet will not upload in TIIMES
Title | Details
Control Number
SAP number
Notification Number
Project Name & Location
Client Name
End User Name
DEC / PMC / EPC Name
DEC / PMC / EPC Number
Vendor Name
PO Number (Client PO on Vendor)
Sub Vendor
PO Number (Vendor PO on Sub Vendor)
Inspection Location
Inspection Date(s)

## Item Description
Po Item No. | Item Code | Item Description | Unit | Po Quantity | Offered Quantity | Accepted Quantity (Please verify thouroghly before using this Column for IRN) | Cumulative Accepted Quanitity (for IRN Only)
30 | CAT3148 | VALVES | PC | 1 | 1 | 1
1 |  | TAG NO. 02-FCV-201A, 02-FCV-202A, 02-FCV-201B, 02-FCV-202B, AS PER DRAWING NO.DIM0001872020_001, INS0001872020_001 | number | 4 | 4 | 4 |  | number
2 |  | TAG NO. 02-HV-206A, 02-HV-206B, AS PER DRAWING NO.DIM0001872020_002, INS0001872020_002 | number | 2 | 2 | 2 | 2 | meter
40 | CAT3148 | SPARES | PC | 1 | 1 | 1 | 1 | km
1 |  | VALVE REPAIR KIT, H034223 | number | 1 | 1 | 1 | 1 | meter (number)
2 |  | ACTUATOR REPAIR KIT, BC9, 250496 | number | 1 | 1 | 1 | 1 | km (number)
3 |  | VALVE REPAIR KIT, MA0041901 | number | 1 | 1 | 1 | 1 | each
4 |  | ACTUATOR REPAIR KIT, MA0127429 | number | 1 | 1 | 1 | 1 | Piece
5 |  | SOV, 51420-6-2R+III-24V-DC-25-LD | number | 2 | 2 | 2 | 2 | Test sample
6 |  | AFR, AW20-N02G1-2-B | number | 1 | 1 | 1 | 1 | AU - All Unit
7 |  | LIMIT SWITCH, KC2A3A3NGRNN | number | 1 | 1 | 1 | 1 | lot
8 |  | POSITIONER, ND9102HN-A3-CE | number | 1 | 1 | 1 | 1 | Set
Running Meter
kg
metric ton (tonne)
ton
cubic millimetre
cubic centimeter
cubic meter
cubic inch
cubic foot
mm
cm
in
foot
mile
yard
liter
kl
cl
ml
g
lb
oz
Sq. mm
Sq. cm
Sq. meter
Sq. in
Sq. foot

## Reference Documents
Sr. No. | Document Name | Client Document Number | Vendor Document Number | Approval Status
1 | PR/MR/ARM | Not Applicable | Not Applicable | Not Applicable
2 | QAP/ITP/QCP | 0G02G-IEX-G00-QC-0001 REV.4 | QAPLAN-02632-En | Approved as Noted
3 | Drawing(s) | Not Applicable | DIM0001872020_001 & 002, INS0001872020_001& 002 | Approved as Noted
4 | Procedure(s) | Not Applicable | Not Applicable | Not Applicable
5 | Datasheet(s) | Not Applicable | Not Applicable | Not Applicable
6 | Others (Specify) | Not Applicable | Not Applicable | Not Applicable

## Stages Witnessed
Stages Witnessed
QAP Sr. No.8.1, Body Pressure Test 10%(min.01No) @ 31 Kg/cm2 for RE series valve -- No visible leakage observed during testing.
QAP Sr. No.8.1, Seat leakage test 10% (min.01No) @ 4Kg/cm2 for RE series Valve -- Found 33ml/minute.
QAP Sr. No.8.1, Body Pressure test 10% (min.01No) @7.4 Kg/cm2 for 4000 series Valve -- No bubble found
QAP Sr. No.8.1, Seat leakage test 10% (min.01No) @7.4 Kg/cm2 for 4000 series Valve -- No bubble found
QAP Sr. No.8.1, Open, close operation and stroke time 10% (min.01No) of each size and type -- Found 3.43 seconds to open and 2.87 seconds to close for Tag No. 02-FCV-202A and 0.72 seconds to pen and 0.35 Seconds to close for Tag No. 02-HV-206B.
QAP Sr. No.8.1, Fail safe condition 10%(min.01No) For RE series Valve -- Electric failure found Close instead of Last
QAP Sr. No.8.1, Fail safe condition 10%(min.01No) for 4000 Series Valve -- Found as per drawing.
QAP Sr. No.8.1, Final visual inspection 10% (min.01No) of each type/ size -- Found as per drawing.
QAP Sr. No.8.1, Major dimension inspection 10% (min.01No) of each size and type -- Found as per drawing.
QAP Sr. No.8.1, Model verification 10%(min.01No) of each type and size -- Found as per draiwng.

## Document reviewed
Document reviewed
QAP Sr. No.1.1, Pressure retaining Part material (Body, Body Cap and Blind flange) certificates -- Found to meet the material specification and manufacturer procedure requirements.
QAP Sr. No.1.1, Ball segment test certificate -- Found in order
QAP Sr. No.3.2, Valve final testing report -- Found in order
QAP Sr. No.7.2, Functional test report for control valve & on-off valve -- Found satisfactory

## Details of measuring instrument
Sr. No. | Detail of Equipment(s) / Instrument(s) | Range | ID | Validity till Date | Calibration Certificate Number | NABL / OTHER CERT. BODIES / NABL Traceability (type Yes wherever applicable) | NON-NABL (type Yes wherever applicable)
1 | Pressure Gauge | 0- 16 Kg/cm2 | 3276PG10040 | 27.07.2023 | 20220728-10475-44 Dtd.30.07.2022 | Yes |  | Yes
2 | Measure Tape | 0-5 meter | ISC-MT-002 | 31.08.2023 | 20220801-10475-18 Dtd.03.08.2022 | Yes |  | No
3 | Vernier Caliper | 0-300mm | ISC-VC-001 | 30.05.2023 | 20220531-10475-80 Dtd.02.06.2022 | Yes

## Areas of concerns
Areas Of Concern
Electric failure found "Close" instead of "Last" for RE series Valves.

## Pending Activities
Pending Activities from this visit
None

## Conclusion
Note: Data filled in this sheet will not upload in TIIMES
Non Conformities raised / Discrepancies observed during Inspection (If Any, Mention TUV India NCR Number ):
Identification of Inspected Item(s):
Conclusion (Acceptable / Not Acceptable / Acceptance subject to):
IRN can be issued for PO Item numbers:
Expenses:
Remarks: