## Notes
Notes:
Data filled in General and conclusion Sections will not upload in TIIMES. Please use these sections to keep data ready for copy paste.
Data in Item Description columns of Accepted Quantity and cumulative Accepted quantity must be verified thoroughly before uploading in TIIMES.
Pending activity, Areas of concern & Details of measuring instruments sheets are applicable for IVR.
Select options from drop down list for unit of measurement (Item Description) & certifying body of measuring instruments (Details of measuring instruments).
Do not modify this format.
To start next row in cell itself use below shortcut: press 'alt + Enter' keys together. Alt + Enter

## General
Note: - Data filled in this sheet will not upload in TIIMES
Title | Details
Control Number
SAP number
Notification Number
Project Name & Location
Client Name
End User Name
DEC / PMC / EPC Name
DEC / PMC / EPC Number
Vendor Name
PO Number (Client PO on Vendor)
Sub Vendor
PO Number (Vendor PO on Sub Vendor)
Inspection Location
Inspection Date(s)

## Item Description
Po Item No. | Item Code | Item Description | Unit | Po Quantity | Offered Quantity | Accepted Quantity (Please verify thouroghly before using this Column for IRN) | Cumulative Accepted Quanitity (for IRN Only)
. | . | AIRTEC REFRIGERATION AND OXYGEN CO. LTD. / PO to SHELL N TUBE PVT. LTD -PD-SHU/2022/11/OPR0015/F0331 REV.0 DT -14.11.2022 | [5 empty] | number
1 | SBALVAPORI01633 | Extruded Aluminium Fins Atmospheric Vaprisers with skid mounted frame ( with SS wire mash) , Capacity 3100 Nm3/hr, | each | 4 | 1 | 1 | 1 | meter
. | . | Mfg. sr.no. 2022-23/161 A & B | [5 empty] | km
meter (number)
km (number)
each
Piece
Test sample
AU - All Unit
lot
Set
Running Meter
kg
metric ton (tonne)
ton
cubic millimetre
cubic centimeter
cubic meter
cubic inch
cubic foot
mm
cm
in
foot
mile
yard
liter
kl
cl
ml
g
lb
oz
Sq. mm
Sq. cm
Sq. meter
Sq. in
Sq. foot

## Reference Documents
Sr. No. | Document Name | Client Document Number | Vendor Document Number | Approval Status
1 | PR/MR/ARM | NA | NA | NA
2 | QAP/ITP/QCP | NA | VPEXP0583 REV. 0 | Approved by AIRTECH
3 | Drawing(s) | NA | G.A. FOR AMBIENT VAPOURISER SNT-3100-L2 - SNT/VPEXP0583-301-L2 REV.0 | Approved by AIRTECH
4 | Procedure(s) | NA | NA | NA
5 | Datasheet(s) | NA | NA | NA
6 | Others (Specify) | NA | NA | NA

## Stages Witnessed
Stages Witnessed
ITP CL 7- Pneumatic pressure test - Vendor offered the set 2022-23/161 A & B ( excluding interconnecting piping between the part A & B) for penumatic test @ 43 KG/CM2 for 30 min. duration. The test media used was Nitrogen. During the test period no presssure drop or leakage observed. Soap water applied on all weld joints and no air bubbles observed as part of leakage, hence penumatic test is acceptable.
Name plate verified and found in order.

## Document reviewed
Document reviewed
ITP CL -1 Raw material MTC, MIR reviewed and found in order.
ITP CL -2 WPS , PQR reviewed and found in order.
ITP CL -3 Alignement and fit up report reviewed and found in order.
ITP CL 4 LPT report reviewed and found in order.
ITP CL 5 Degressing report reviewed and found in order.
ITP CL 6 Dimensional /visual report reviewed and found in order.
ITP CL 7 Penumatic test pressurel report reviewed and found in order.
Calibration test reports reviewed and found in order.
Reviewed loat test report of the skid for Tag no

## Details of measuring instrument
Sr. No. | Detail of Equipment(s) / Instrument(s) | Range | ID | Validity till Date | Calibration Certificate Number | NABL / OTHER CERT. BODIES / NABL Traceability (type Yes wherever applicable) | NON-NABL (type Yes wherever applicable)
1 | Pressure gauge | 0-100 kg/cm2 | 90253516-41-10 | 2.08.2023 | 220801/36/PRE | Yes |  | Yes
2 | Pressure gauge | 0-100 kg/cm2 | 900011N7 | 7.09.2023 | 220908/04/PRE | Yes |  | No

## Areas of concerns
Areas Of Concern

## Pending Activities
Pending Activities from this visit

## Conclusion
Note: Data filled in this sheet will not upload in TIIMES
Non Conformities raised / Discrepancies observed during Inspection (If Any, Mention TUV India NCR Number ):
Identification of Inspected Item(s):
Name plate by Mfg. and TUV hard stamp on the name plate as " "
Conclusion (Acceptable / Not Acceptable / Acceptance subject to):
Acceptable
IRN can be issued for PO Item numbers:
Expenses:
Remarks: