## Notes
Notes:
Data filled in General and conclusion Sections will not upload in TIIMES. Please use these sections to keep data ready for copy paste.
Data in Item Description columns of Accepted Quantity and cumulative Accepted quantity must be verified thoroughly before uploading in TIIMES.
Pending activity, Areas of concern & Details of measuring instruments sheets are applicable for IVR.
Select options from drop down list for unit of measurement (Item Description) & certifying body of measuring instruments (Details of measuring instruments).
Do not modify this format.
To start next row in cell itself use below shortcut: press 'alt + Enter' keys together. Alt + Enter

## General
Note: - Data filled in this sheet will not upload in TIIMES
Title | Details
Control Number
SAP number
Notification Number
Project Name & Location
Client Name
End User Name
DEC / PMC / EPC Name
DEC / PMC / EPC Number
Vendor Name
PO Number (Client PO on Vendor)
Sub Vendor
PO Number (Vendor PO on Sub Vendor)
Inspection Location
Inspection Date(s)

## Item Description
Po Item No. | Item Code | Item Description | Unit | Po Quantity | Offered Quantity | Accepted Quantity (Please verify thouroghly before using this Column for IRN) | Cumulative Accepted Quanitity (for IRN Only)
1 | -- | Motor Electric fire pump Supplying, installation, testing and commissioning of electric driven main fire pump suitable for automatic operation and consisting of following: complete in all respect as required, a) Horizontal type, multistage, cetrifugal, split casing pump of cast iron body & bronze impeller with stainless steel shaft, meachnical seal to ensure a minimum pressure of 3.5 kg/sq.cm at highest and farthest outlet at specified flow of 2280 LPM at 120 m. head confirming to IS 1520, b) Suitable HP sq. cage induction motor, TEFC, synchronous. speed 1500 rpm, suitable for operating on 415 volts +/- 10%, 3 phase 50 Hz, AC with IP 55 protection for enclosure, horizontal foot mounted type with Class - 'F' insulation, confirming to IS-325. c) M.S Fabricated common base plate, coupling, coupling gaurd, foundation bolts etc. as required d) Suitable cement concrete foundation duly plastered with anti-vibration pads. | Set | 2 | 2 | 2 | 2 | number
2 | -- | Diesel Engine Driven Pump Supplying, installation, testing and commissioning of diesel engine driven main fire pump suitable for automatic operation and consisting of following: complete in all respect as required, a) Horizontal type, multistage, cetrifugal, split casing pump of cast iron body & bronze impeller with stainless steel shaft, meachnical seal to ensure a minimum pressure of 3.5 kg/sq.cm at highest and farthest outlet at specified flow of 2280 LPM at 120 m. head confirming to IS 1520, b) Suitable HP, 1500 rpm water cooled with radiator, diesel engine confirming to relevant BS & IS standard complete with auto starting mechanism, 12 volts / 24 volts electric starting equipment, diesel tank, exhaust pipe extended upto 1 m. outside pump house duly insulated with 50 mm thick glass wool with 1.0 mm thick aluminium sheet cladding, residential silencer, instruments and protection as per standard specification, stop solenoid for auto stop in event of fault with audio indications, painted with post office red colour etc. as required. c) M.S Fabricated common base plate, coupling, coupling gaurd, foundation bolts etc. as required d) Suitable cement concrete foundation duly plastered with anti-vibration pads. | Set | 1 | 1 | 1 | 1 | meter
km
meter (number)
km (number)
each
Piece
Test sample
AU - All Unit
lot
Set
Running Meter
kg
metric ton (tonne)
ton
cubic millimetre
cubic centimeter
cubic meter
cubic inch
cubic foot
mm
cm
in
foot
mile
yard
liter
kl
cl
ml
g
lb
oz
Sq. mm
Sq. cm
Sq. meter
Sq. in
Sq. foot

## Reference Documents
Sr. No. | Document Name | Client Document Number | Vendor Document Number | Approval Status
1 | PR/MR/ARM | Allotment order no. SIMS 139 SE/22-23/865 65 Dated. 14/12/2022 | Not applicable | Provided by M/s. UEE Favourite JV
2 | QAP/ITP/QCP | Kindly find allotment attached to correlate with other documents. Complete inspection of units is requested with documents correlation. | Not applicable | Provided by M/s. UEE Favourite JV over email dated 01.06.2023
3 | Drawing(s) | Not applicable | Not applicable | Not applicable
4 | Procedure(s) | Not applicable | Not applicable | Not applicable
5 | Datasheet(s) | Not applicable | Datasheet for For PO Sr. no. 1 & 2, DSM 125/40 | Approved by M/s. UEE Favourite JV
6 | Others (Specify) | Not applicable | Not applicable | Not applicable

## Stages Witnessed
Stages Witnessed
PO Sr. No. refer from Allotment order no. SIMS 139 SE/22-23/856-65, Dated. 14/12/2022, Annexure - B
For PO Sr. No. 1 - Visual inspection of pump carried out - Found no injurious surface defect observed during inspection, paint quality visually checked - found free from pill off, sagging, over coat, spatter marks etc. . Pump model, rating, flow, head, rpm etc verify with technical data sheet provide by M/s. Favourite Electrical - found in order.
For PO Sr. No. 2 - Visual inspection of pump carried out - Found no injurious surface defect observed during inspection, paint quality visually checked - found free from pill off, sagging, over coat, spatter marks etc. . Pump model, rating, flow, head, rpm etc verify with technical data sheet provide by M/s. Favourite Electrical - found in order.

## Document reviewed
Document reviewed
Routine test certificate for motor reviewed for its technical content only as declared by manufacturer and endorsed by J&C - Found to applicable technical datasheet, PO and other specification requirements.
Routine test certificate for pump reviewed for its technical content only as declared by manufacturer and endorsed by J&C - Found to applicable technical datasheet, PO and other specification requirements.
Test certificate for engine reviewed/noted for its technical content only as declared by manufacturer and endorsed by J&C - Found to applicable technical datasheet, PO and other specification requirements.
Visual inspection report reviewed - Found in order.
Internal inspection report reviewed - Found in order.
Hydro test report reviewed - found as per datasheet requirments.
Impeller balancing report reviewed - found in order.
Performance test report reviewed - found as per datasheet requirements.

## Details of measuring instrument
Sr. No. | Detail of Equipment(s) / Instrument(s) | Range | ID | Validity till Date | Calibration Certificate Number | NABL / OTHER CERT. BODIES / NABL Traceability (type Yes wherever applicable) | NON-NABL (type Yes wherever applicable)
| Not applicable | [6 empty] | Yes
No

## Areas of concerns
Areas Of Concern
M/s. UEE Favourite JV' email for area of concern of IVR-010104174723/1-1, Rev.0 as follows For order sr. no. 1, 2 - While review of routine test certificate of motor, it is found as per IS 12615 instead of order require IS 325. - Compliace report given by client and approved by M/s. UEE Favourite JV For order sr. no. 1, 2 - While review of test certificate of pump, it is found as per IS ISO 9906 instead of order require IS 1520. - vendor recertify as IS1937 : 1998, revise test certificate reviewed. - Compliace report given by client and approved by M/s. UEE Favourite JV For order sr. no. 2 - Diesel tank, insulation of glass wool with 1.0 mm aluminium sheet cladding over exhaust pipe not carried out by Vendor (M/s. Jakson & company) - Client reply as " For order sr. no. 2 - solenoid for auto stop in event of fault with audio not provided by Vendor (M/s. Jakson & company) - client reply as "

## Pending Activities
Pending Activities from this visit

## Conclusion
Note: Data filled in this sheet will not upload in TIIMES
Non Conformities raised / Discrepancies observed during Inspection (If Any, Mention TUV India NCR Number ):
None
Identification of Inspected Item(s):
Conclusion (Acceptable / Not Acceptable / Acceptance subject to):
IRN can be issued for PO Item numbers:
Expenses:
Remarks: